## Reversion
Reversion Record
Date | Version | Description | Editor | Auditor
2023-05-25 | V0 | Initial Version |  | zp Gao
2023-05-25 | V1.0 |  |  | zp Gao

## Comm
通信方式说明： 1、物理层通信方式支持：RS485/以太网; 2、通信协议为Modbus-RTU/Modbus-TCP； 3、HMI作为主机，EMS作为从机； 4、EMS默认Modbus-RTU设备地址为1、波特率为9600； 5、EMS默认Modbus-TCP端口； Communication Method Description: 1. Physical layer communication methods supported: RS485/Ethernet; 2. Communication protocol: Modbus-RTU/Modbus-TCP; 3. HMI acts as the master, EMS as the slave; 4. Default Modbus-RTU device address for EMS is 1, baud rate is 9600; 5. Default Modbus-TCP port for EMS;

## Data Overview Page
EMS Information
以下所有报文字节序：int32 ABCD 大端模式，低地址为AB，高地址为CD，例如：0x1101~0x1102数据为 AB CD ，0x1101 发AB，0x1102发CD int32类型和int64类型的数据都留下小数点后两位 实际值=报文值/100 （最后值 本身是一个带方向的整数） For all the following telegrams: The byte order is int32 ABCD Big-Endian, with the low address as AB and the high address as CD. For example, for data at addresses 0x1101 to 0x1102, 0x1101 sends AB and 0x1102 sends CD. All int32 and int64 data types should retain two decimal places. The actual value is calculated as the telegram value divided by 100. (The final value is an integer with a sign).
| 名称 | Name | 定义 | Name | Function Code | Addr | Read/Write Type | Unit | Type | Definition | Remarks
Basic information
Data Reading Example |  | Rx:01 04 10 00 00 16 75 04 Tx:01 04 2C 07 E7 00 0C 00 0C 00 14 00 14 00 0B 00 00 00 03 00 0A 00 FA 00 6E 00 02 00 03 00 03 00 03 00 03 00 A0 00 03 00 02 00 03 00 00 00 01 07 C3
| 时间-年 | DateYear |  | Time - Year | 0x04 0x06 | 0x1000 | RW | Year | u16 | 0~99
| 时间-月 | DateMonth |  | Time - Month | 0x04 0x06 | 0x1001 | RW | Month | u16 | 1~12
| 时间-日 | DateDay |  | Time - Day | 0x04 0x06 | 0x1002 | RW | Day | u16 | 1~31
| 时间-时 | DateHour |  | Time - Hour | 0x04 0x06 | 0x1003 | RW | Hour | u16 | 0~23
| 时间-分 | Dateminute |  | Time - Minute | 0x04 0x06 | 0x1004 | RW | Minute | u16 | 0~59
| 时间-秒 | DateYSecond |  | Time - Second | 0x04 0x06 | 0x1005 | RW | Second | u16 | 0~59
| 存储状态 | StorageState |  | Storage State | 0x04 | 0x1006 | R0 | - | u16 | 0：Normal； 1：Abnormal
| 堆数量 | StackNum |  | Stack Count | 0x04 | 0x1007 | R0 | - | u16
| 当前堆中的簇数量 | ClusterNumofStack |  | Current Stack Cluster Count | 0x04 | 0x1008 | R0 | - | u16
| 当前簇中的单体电压数量 | VoltageNumofCluster |  | Current Cluster Cell Voltage Count | 0x04 | 0x1009 | R0 | - | u16
| 当前簇中的单体温感数量 | NtcNumofCluster |  | Current Cluster Cell Temperature Count | 0x04 | 0x100A | R0 | - | u16
| PCS数量 | PcskNum |  | PCS Count | 0x04 | 0x100B | R0 | - | u16
| 电表数量 | MeterNum |  | Meter Count | 0x04 | 0x100C | R0 | - | u16 |  |  |  | --
| 空调数量 | AirNum |  | AC Count | 0x04 | 0x100D | R0 | - | u16 |  |  |  | --
|  | DoorNum |  |  | 0x04 | 0x100E | R0 | - | u16 |  |  |  | --
| 消防数量 | FireNum |  | Fire Protection Count | 0x04 | 0x100F | R0 | - | u16 |  |  |  | --
| 历史故障总数量 | FaultNum |  | Total Historical Fault Count | 0x04 | 0x1010 | R0 | - | u16 |  |  |  | --
| 风扇数量 | FANNum |  | Fan Count | 0x04 | 0x1011 | R0 | - | u16 |  |  |  | --
| TMS数量 | TMSNum |  | TMS Count | 0x04 | 0x1012 | R0 | - | u16 |  |  |  | --
| DI界面数量 | DINum |  | DI Interface Count | 0x04 | 0x1013 | R0 | - | u16 |  |  |  | --
| 除湿机数量 | dehumNum |  | Dehumidifier Count | 0x04 | 0x1014 | R0 | - | u16 |  |  |  | --
| UPS数量 | UPSumNum |  | UPS Count | 0x04 | 0x1015 | R0 | - | u16 |  |  |  | --
| PV逆变总数 | PVNum |  | Total PV Inverter Count | 0x04 | 0x1016 | R0 | - | u16
| DCDC数量 | DCDCNum |  | DCDC Count | 0x04 | 0x1017 | R0 | - | u16
| 充电桩 | ChargerNum |  | EVSE Count | 0x04 | 0x1018 | R0 | - | u16
| 柴发 | DieselNum |  | Diesel Gen Count | 0x04 | 0x1019 | R0 | - | u16
| pack数量（从机数量） |  |  | Pack Count (Slave Count) | 0x04 | 0x101A | R0 | - | u16 |  | Defaults to the number of slaves in cluster 0. The number of cells and temperatures in each pack is calculated from the total number of voltages and temperatures in the cluster.
| ATS数量 | ATSNum |  | ATS Count | 0X04 | 0X101B | R0 | - | U16
| 充电座数量 |  |  | Charging Receptacle Count | 0X04 | 0X101C | R0 |  | U16
| ACDC数量 |  |  | ACDC Count | 0X04 | 0X101D | R0 |  | U16
Pointer (Write Operation) | [11 empty] | 说明： 1、HMI先发送“写入”指令给EMS，告知EMS需要读取的数据。 2、EMS将对应数据映射到对应的数据区域。 3、HMI发送“读”的指令，读取映射区域的数据 这个流程，第2步执行完后会通知hmi数据已准备好吗？ MODBUS已经定义过一个写成功的指令了
Data Reading Example |  | Rx:01 06 20 05 00 00 92 0B Tx:01 06 20 05 00 00 92 0B 对单个设备编号进行写入（举例为写入电表编号）
| 堆编号 | StackAddr. |  | Stack Number | 0x04 0x06 | 0x2000 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| 簇编号 | ClusterAddr. |  | Cluster Number | 0x04 0x06 | 0x2001 | RW | - | u16 | The software defaults to 0, while the display starts from 1. | Default points to the first heap, cluster, cell, temperature sensor, PCS, |  | --
| 单体电压编号 | CellVoltAddr. |  | Cell Voltage Number | 0x04 0x06 | 0x2002 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| 电池温感编号 | CellTempAddr. |  | Battery Temperature Sensor Number | 0x04 0x06 | 0x2003 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| PCS编号 | PcsAddr |  | PCS Number | 0x04 0x06 | 0x2004 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| 电表编号 | MeterAddr |  | Meter Number | 0x04 0x06 | 0x2005 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| 空调编号 | AirAddr |  | Air Conditioner Number | 0x04 0x06 | 0x2006 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| 消防编号 | FireAddr |  | Fire Protection Number | 0x04 0x06 | 0x2007 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| 门禁编号 | DoorAddr |  | Access Control Number | 0x04 0x06 | 0x2008 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| 风扇编号 | FANAddr |  | Fan Number | 0x04 0x06 | 0x2009 | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| TMS编号 | TMSAddr |  | TMS Number | 0x04 0x06 | 0x200A | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| DI编号 | DIAddr |  | DI Number | 0x04 0x06 | 0x200B | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| 除湿机编号 | dehumAddr |  | Dehumidifier Number | 0x04 0x06 | 0x200C | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| UPS编号 | UPSAddr |  | UPS Number | 0x04 0x06 | 0x200D | RW | - | u16 | The software defaults to 0, while the display starts from 1. |  |  | --
| PV编号 | PVAddr |  | PV Number | 0x04 0x06 | 0x200E | RW | - | u16 | The software defaults to 0, while the display starts from 1.
| DCDC编号 | DCAddr |  | DCDC Number | 0x04 0x06 | 0x200F | RW | - | u16 | The software defaults to 0, while the display starts from 1.
| 充电桩编号 | ChargerAddr |  | Charging Pile Number | 0x04 0x06 | 0x2010 | RW | - | u16 | The software defaults to 0, while the display starts from 1.
| 柴发编号 | DieselAddr |  | Diesel Generator Number | 0x04 0x06 | 0x2011 | RW | - | u16 | The software defaults to 0, while the display starts from 1.
| PACK 编号 |  |  | PACK Number | 0x04 | 0x2012 | RW | - | u16 | The software defaults to 0, while the display starts from 1.
| ATS编号 | ATSAddr |  | ATS Number | 0X04 0X06 | 0X2013 | RW | - | u16 | The software defaults to 0, while the display starts from 1.
| 充电座编号 |  |  | Charging Receptacle Number | 0X04 0X06 | 0X2014 | RW |  | u16 | The software defaults to 0, while the display starts from 1.
| ACDC编号 |  |  | ACDC Number | 0X04 0X06 | 0X2015 | RW |  | u16 | The software defaults to 0, while the display starts from 1.
| 历史 故障 | HistiryError |  | Historical Fault | 0x04 0x06 | 0x2100 | RW | - | u16 | The software defaults to 0, while the display starts from 1. | Here, "1" refers to the most recent fault. |  | --
| 预留 |  |  | Reserved
Dashboard Homepage (Overview Interface)
| Data Reading Example | Rx:01 04 11 00 00 40 F4 C6 Tx:01 04 80 00 04 00 00 00 01 FF ED 29 79 FF 43 9E B2 00 0A 00 C4 00 04 EF 05 00 00 00 00 00 00 02 22 00 00 00 00 3B 9A C9 FF 00 00 00 00 00 04 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 00 01 00 00 00 DE 00 06 00 00 00 7B 00 03 00 00 02 2B 00 05 00 00 02 9A 00 04 00 00 00 DE 00 07 00 00 16 18 00 02 00 00 00 6F 00 08 00 00 0C 96 00 01 2E 7D
| 名称 | Name | 定义 | Name |  | Addr |  | Unit | Type | 定义 | remarks
| 储能运行状态 | EisWorkingmode |  | Energy Storage Running Status | 0x04 | 0x1100 | R0 | - | u16 | 0x01: Shutdown 0x02: Standby 0x04: Charging 0x08: Discharging 0x10: Fault 0x20: Zero Power 0xAA: No Communication |  |  | 系统级状态显示； 电量灯充、放电、待机状态显示；
| 综合效率 | EisEfficient |  | Overall Efficiency | 0x04 | 0x1101~0x1102 | R0 | 0.01 | int32 | 0~1 |  |  | --
| 昨日收益 | EisDailyProfit |  | Yesterday's Revenue | 0x04 | 0x1103~0x1104 | R0 | 0.01 元 | int32 |  |  |  | --
| 总收益 | EisTotalProfit |  | Total Revenue | 0x04 | 0x1105~0x1106 | R0 | 0.01 万元 | int32 |  |  |  | --
| 当日充电量 | EisDailyChgEnergy |  | Daily Charge Amount | 0x04 | 0x1107~0x1108 | R0 | 0.01 kWh | int32 |  |  |  | --
| 当日放电量 | EisDailyDchgEnergy |  | Daily Discharge Amount | 0x04 | 0x1109~0x110A | R0 | 0.01 kWh | int32 |  |  |  | --
| 总充电量 | EisTotalChgEnergy |  | Total Charge Amount | 0x04 | 0x110B~0x110E | R0 | 0.01 kWh | int64 | Use 8 bytes | Endianness: ABCD Big-Endian Mode |  | --
| 总放电量 | EisTotalDchgEnergy |  | Total Discharge Amount | 0x04 | 0x110F~0x1112 | R0 | 0.01 kWh | int64 | Use 8 bytes | Endianness: ABCD Big-Endian Mode |  | --
| PCS运行状态 | PcsWorkingmode |  | PCS Running Status | 0x04 | 0x1123 | R0 | - | u16 | 0x01: Normal Operation 0x02: Fault 0x04: Shutdown 0xAA: No Communication |  |  | 系统级PCS状态，需要结合“'单簇PCS状态”信息显示；若发生簇告警，则状态灯中的其中1-2个显示告警即可。
| 电表运行状态 | MeterWorkingmode |  | Meter Running Status | 0x04 | 0x1124 | R0 | - | u16 | 0x01: Normal Operation 0x02: Fault 0x04: Shutdown 0xAA: No Communication |  |  | 关联系统指示灯中的1个（电表），空调、液冷机组故障时，该灯闪亮告警
| BMS运行状态 | BmsWorkingmode |  | BMS Running Status | 0x04 | 0x1125 | R0 | - | u16 | 0x01: Normal Operation 0x02: Fault 0x04: Shutdown 0xAA: No Communication |  |  | 系统级BMS(电池）状态，需要结合簇运行信息显示；若发生簇告警，则状态灯中的其中1-2个显示告警即可。
| 空调运行状态 | AirWorkingmode |  | AC Running Status | 0x04 | 0x1126 | R0 | - | u16 | 0x01: Normal Operation 0x02: Fault 0x04: Shutdown 0xAA: No Communication |  |  | 关联系统指示灯中的1个，空调、液冷机组故障时，该灯闪亮告警
| 1号设备类型 | Equipment 1 Type |  | Device 1 Type | 0x04 | 0x1127 | R0 | - | u16 | 0: Not Used 1: Grid 2: Energy Storage Battery 3: Photovoltaic 4: Load 5: Diesel Generator 6: Wind Turbine 7: Load 2 8: Energy Storage Battery 2 9: Charging Pile 10: DC Input (Charging Receptacle) 11: Other |  |  | --
| 1号设备功率 | Equipment 1 power |  | Device 1 Power | 0x04 | 0x1128~0x1129 | R0 | 0.01 KW | int32 | It has units, with positive and negative signs. |  |  | --
| 2号设备类型 | Equipment 2 Type |  | Device 2 Type | 0x04 | 0x112A | R0 | - | u16 | 0: Not Used 1: Grid 2: Energy Storage Battery 3: Photovoltaic 4: Load 5: Diesel Generator 6: Wind Turbine 7: Load 2 8: Energy Storage Battery 2 9: Charging Pile 10: DC Input (Charging Receptacle) 11: Other |  |  | --
| 2号设备功率 | Equipment 2 power |  | Device 2 Power | 0x04 | 0x112B~0x112C | R0 | 0.01 KW | int32 | It has units, with positive and negative signs. |  |  | --
| 3号设备类型 | Equipment 3 Type |  | Device 3 Type | 0x04 | 0x112D | R0 | - | u16 | 0: Not Used 1: Grid 2: Energy Storage Battery 3: Photovoltaic 4: Load 5: Diesel Generator 6: Wind Turbine 7: Load 2 8: Energy Storage Battery 2 9: Charging Pile 10: DC Input (Charging Receptacle) 11: Other |  |  | --
| 3号设备功率 | Equipment 3 power |  | Device 3 Power | 0x04 | 0x112E~0x112F | R0 | 0.01 KW | int32 | It has units, with positive and negative signs. |  |  | --
| 4号设备类型 | Equipment 4 Type |  | Device 4 Type | 0x04 | 0x1130 | R0 | - | u16 | 0: Not Used 1: Grid 2: Energy Storage Battery 3: Photovoltaic 4: Load 5: Diesel Generator 6: Wind Turbine 7: Load 2 8: Energy Storage Battery 2 9: Charging Pile 10: DC Input (Charging Receptacle) 11: Other |  |  | --
| 4号设备功率 | Equipment 4 power |  | Device 4 Power | 0x04 | 0x1131~0x1132 | R0 | 0.01 KW | int32 | It has units, with positive and negative signs. |  |  | --
| 5号设备类型 | Equipment 5 Type |  | Device 5 Type | 0x04 | 0x1133 | R0 | - | u16 | 0: Not Used 1: Grid 2: Energy Storage Battery 3: Photovoltaic 4: Load 5: Diesel Generator 6: Wind Turbine 7: Load 2 8: Energy Storage Battery 2 9: Charging Pile 10: DC Input (Charging Receptacle) 11: Other |  |  | --
| 5号设备功率 | Equipment 5 power |  | Device 5 Power | 0x04 | 0x1134~0x1135 | R0 | 0.01 KW | int32 | It has units, with positive and negative signs. |  |  | --
| 6号设备类型 | Equipment 6 Type |  | Device 6 Type | 0x04 | 0x1136 | R0 | - | u16 | 0: Not Used 1: Grid 2: Energy Storage Battery 3: Photovoltaic 4: Load 5: Diesel Generator 6: Wind Turbine 7: Load 2 8: Energy Storage Battery 2 9: Charging Pile 10: DC Input (Charging Receptacle) 11: Other |  |  | --
| 6号设备功率 | Equipment 6 power |  | Device 6 Power | 0x04 | 0x1137~0x1138 | R0 | 0.01 KW | int32 | It has units, with positive and negative signs. |  |  | --
| 7号设备类型 | Equipment 7 Type |  | Device 7 Type | 0x04 | 0x1139 | R0 | - | u16 | 0: Not Used 1: Grid 2: Energy Storage Battery 3: Photovoltaic 4: Load 5: Diesel Generator 6: Wind Turbine 7: Load 2 8: Energy Storage Battery 2 9: Charging Pile 10: DC Input (Charging Receptacle) 11: Other |  |  | --
| 7号设备功率 | Equipment 7 power |  | Device 7 Power | 0x04 | 0x113A~0x113B | R0 | 0.01 KW | int32 | It has units, with positive and negative signs. |  |  | --
| 8号设备类型 | Equipment 8 Type |  | Device 8 Type | 0x04 | 0x113C | R0 | - | u16 | 0: Not Used 1: Grid 2: Energy Storage Battery 3: Photovoltaic 4: Load 5: Diesel Generator 6: Wind Turbine 7: Load 2 8: Energy Storage Battery 2 9: Charging Pile 10: DC Input (Charging Receptacle) 11: Other |  |  | --
| 8号设备功率 | Equipment 8 power |  | Device 8 Power | 0x04 | 0x113D~0x113E | R0 | 0.01 KW | int32 | It has units, with positive and negative signs. |  |  | --
| 其他运行状态 | othersWorkingmode |  | Other Running Status | 0x04 | 0x113F | R0 | - | u16 | 0x01: Normal Operation 0x02: Fault 0x04: Shutdown |  |  | --
| 系统总SOC |  |  | System Total SOC | 0x04 | 0x1140 | R0 | - | u16
| 充电合闸状态 |  |  | Charging Contactor Status | 0x04 | 0x1141 | R0 |  | u16 | 0x00: Invalid Value 0x01: Closed 0x02: Open
| 放电合闸状态 |  |  | Discharging Contactor Status | 0x04 | 0x1142 | R0 |  | u16 | 0x00: Invalid Value 0x01: Closed 0x02: Open
| 充电车运行状态 |  |  | EV Charger Running Status | 0x04 | 0x1143 | R0 |  | u16 | 0x00 Invalid Value 0x01 Standby 0x02 Pre-charging 0x03 Pre-charge Successful 0x04 Pre-charge Failed 0x05 Charging 0x06 Discharging 0x07 Fault
| 充电车功能-控制状态 |  | 0-预留；1-充电合闸，2-充电分闸，3-放电合闸，4-放电分闸 | EV Charger Function - Control Status | 0x04 | 0x1144 | R0 |  | u16 | 0 - Reserved 1 - Charging Contactor Closed 2 - Charging Contactor Open 3 - Discharging Contactor Closed 4 - Discharging Contactor Open
| 清除显示屏主界面报警字 |  |  | Clear Main Display Alarm | 0x04 | 0x1145 | R0 |  | u16 | bit-0：0-Normal 1-soc low alarm bit-1：0-Normal 1-Low Fluid Level Alarm
| 系统总SOH |  |  | System Total SOH | 0x04 | 0x1146 | R0 | - | u16
| 当前上网状态 |  | 0-4G模式； 1-网口1配置DHCP； 2-网口2配置DHCP | Current Internet Connection Status | 0x04 | 0x1147 | R0 | - | u16 | 0 - Reserved 1 - 4G Network Mode 2 - Ethernet Port 1 - DHCP 3 - Ethernet Port 2 - DHCP
| 预留 |  |  | Reserved |  | 0x113F~0x11FF | [6 empty] | --
--
Communication status | [12 empty] | --
| 名称 | Name |  | Name |  | Addr |  | Unit | Type |  |  |  | --
| SD卡状态 | SDState |  | SD Card Status | 0x04 | 0x1200 | R0 | - | u16 | 0 - Normal 1 - Abnormal |  |  | --
| SD卡预留 | 预留 |  | SD Card Reserved | 0x04 | 0x1201 | R0 | - | u16 |  |  |  | --
| 网口1网络IP | Wlan1Ip |  | Ethernet Port 1 IP | 0x04 | 0x1202~0x1203 | R0 | - | u32 | Example: 123.456.789.987 | 0x1202 sends 123 and 456, 0x1203 sends 789 and 987. |  | --
| 网口2网络IP | Wlan2Ip |  | Ethernet Port 2 IP | 0x04 | 0x1204~0x1205 | R0 | - | u32 |  | Same as above. |  | --
| 网口1子网掩码 | Wlan1MaskIp |  | Ethernet Port 1 Subnet Mask | 0x04 | 0x1206~0x1207 | R0 | - | u32 |  | Same as above. |  | --
| 网口2子网掩码 | Wlan2MaskIp |  | Ethernet Port 2 Subnet Mask | 0x04 | 0x1208~0x1209 | R0 | - | u32 |  | Same as above. |  | --
| 网口1网关IP | Wlan1GatewayIp |  | Ethernet Port 1 Gateway IP | 0x04 | 0x120A~0x120B | R0 | - | u32 |  | Same as above. |  | --
| 网口2网关IP | Wlan2GatewayIp |  | Ethernet Port 2 Gateway IP | 0x04 | 0x120C~0x120D | R0 | - | u32 |  | Same as above. |  | --
| 4G--运行状态 | 4GState |  | 4G - Running Status | 0x04 | 0x120E | R0 | - | u16 | 0 - Registering 1 - Registered 2 - Waiting for data transmission 3 - Data transmitting" |  |  | --
| U盘状态 | Upanstate |  | USB Drive Status | 0x04 | 0x120F | R0 | - | u16 | 0~65535 |  |  | --
| 4G--GSM网络 | GSM |  | 4G - GSM Network | 0x04 | 0x1210 | R0 | - | u16 | 0 - Not registered 1 - Registered |  |  | 未注册时告警，关联系统指示灯中的1个（信号指示灯）
| 4G--GPRS网络 | GPRS |  | 4G - GPRS Network | 0x04 | 0x1211 | R0 | - | u16 | 0 - Not registered 1 - Registered |  |  | --
| 4G--信号强度 | SignalStrength |  | 4G - Signal Strength | 0x04 | 0x1212 | R0 | - | u16 | Value, 0~65535 |  |  | 型号≤-20dB时告警关联系统指示灯中的1个（信号指示灯）
| 4G-发送成功包计数 | 4Gcount |  | 4G - Successful Packet Count | 0x04 | 0x1213 | R0 | - | u16 | 0~65535 |  |  | --
| 4G--误码率 | ErrorRate |  | 4G - Bit Error Rate | 0x04 | 0x1214 | R0 | - | u16 | Value, 0~65535 |  |  | --
| EMS型号 |  |  | EMS Model | 0x04 | 0x1215 | R0 | - | u16 | 0 - G700 1 - G720
| 系统码允许更新标志 |  |  | System Code Update Allowed Flag | 0x04 | 0x1216 | R0 |  | R0 | 0 - Refresh not allowed; 1 - Refresh allowed
| 系统码允许获取标志 |  |  | System Code Acquisition Allowed Flag | 0x04 | 0x1217 | R0 |  | R0 | 0 - Acquisition not allowed; 1 - Acquisition allowed (EMS will send an "acquisition allowed" signal to the display upon successful acquisition)
| 4G--IMEI | IMEI |  | 4G - IMEI | 0x04 | 0x1220~0x122F | R0 | - | Byte | Saved as 32 bytes, 16 addresses | Big-Endian |  | --
| 4G--CCID | CCID |  | 4G - CCID | 0x04 | 0x1230~0x123F | R0 | - | Byte | Saved as 32 bytes, 16 addresses | Big-Endian |  | --
| 4G--LAC | LAC |  | 4G - LAC | 0x04 | 0x1240~0x1247 | R0 | - | u16 | Value, 0~65535 |  |  | --
| 4G--CI | CI |  | 4G - CI | 0x04 | 0x1248~0x124F | R0 | - | u32 | 4 bytes, 2 addresses |  |  | --
| EMS软件版本号 |  |  | EMS Software Version | 0x04 | 0x1250~0x1257 | R0 | - | u16 | 0~65535 |  |  | --
|  |  |  | System Code | [8 empty] | --
| 系统码 |  |  | Name | [8 empty] | --
| 名称 | Name |  |  |  | Addr |  | Unit | Type |  |  |  | --
|  |  |  | EMS Code | [8 empty] | --
| EMS Code Number | EmsSN |  |  | 0x04 | 0x1300~0x143F | R0 |  |  | DD |  |  | --
--
CLUSTER_DATA(Display according to clusters, cluster view, cluster summary data) | [12 empty] | --
--
| Data reading example | Rx:01 04 30 00 00 20 FE D2 Tx:01 04 40 00 01 00 02 00 00 00 01 21 AE 00 FD 00 01 03 6C 02 93 FF FE FF FE FF FE 00 01 0D EE 00 09 0C 27 00 17 00 42 00 14 00 3D 00 00 00 EC 0C 96 00 3F 00 4B 00 4C 00 00 00 00 00 00 00 00 00 00 00 00 32 0D
| 名称 | Name |  |  |  | Addr |  | Unit | Type | definitions | remarks |  | --
| 簇并网状态（簇输出状态） | ClusterParallelState |  | Cluster Grid-Connection Status (Cluster Output Status) | 0x04 | 0x3000 | R0 |  | u16 | 0 - Not Paralleled (Main Positive/Negative Contactor Not Closed) 1 - Paralleled (Main Positive/Negative Contactor Closed) |  |  | --
| Cluster运行状态 | ClusterWorkingmode |  | Cluster Running Status | 0x04 | 0x3001 | R0 | - | u16 | 1: Charge Prohibited (Rack can discharge, cannot charge); 2: Discharge Prohibited (Rack can charge, cannot discharge); 3: Standby (Rack cannot charge or discharge); 4: Shutdown (Rack cannot charge or discharge); | Overvoltage at full charge (charging prohibited) - Discharge only, no charging Undervoltage (discharge prohibited) - Charge only, no discharging Severe fault (shutdown) - Charging and discharging prohibited Cluster awakened but not paralleled - Status: Standby No fault and after paralleling - Status: Normal |  | 簇3级BMS(电池）显示； 全部位“0：时，结合“系统级BMS(电池）”状态显示；若发生簇告警，则状态灯中的其中1-2个显示告警即可。正常时，结合系统状态显示
| Cluster预充电阶段 | ClusterPrechargePhase |  | Cluster Pre-charging Stage | 0x04 | 0x3002 | R0 | - | u16 | 0xAA: No Communication 0: Disconnected (Main Positive, Main Negative, Pre-charge Open) 1: Starting Grid Connection (Pre-charge Closed, Main Negative Open, Main Positive Open) 2: Grid Connecting (Pre-charge, Main Positive, and Main Negative Closed) 3: Grid Connection Successful (Pre-charge Open, Main Positive, and Main Negative Closed) 4: Grid Connection Failed |  |  | --
| Cluster接触器状态 | ClusterConnectionState |  | Cluster Contactor Status | 0x04 | 0x3003 | R0 | - | u16 | 0x0: Open, 0x1: Closed; Bit0: Main Contactor Status; Bit1: Pre-charge Contactor Status; Bit2: Main Negative Contactor Status; Bit3: Disconnect Switch Status; |  |  | --
| Cluster当前电池总电压 | ClusterTotalVolt |  | Cluster Current Total Battery Voltage | 0x04 | 0x3004 | R0 | 0.1V | u16 | 0 to 6553.5V |  |  | --
| Cluster当前电池总电流 | ClusterTotalCurrent |  | Cluster Current Total Battery Current | 0x04 | 0x3005 | R0 | 0.1A | s16 | Charging current is negative, discharging is positive | Current of Battery Cluster
| Cluster充放电指示 | ClusterChgorDChgState |  | Cluster Charge/Discharge Indication | 0x04 | 0x3006 | R0 | - | u16 | 0x0: Static; 0x1: Discharging; 0x2: Charging | Battery Charging/Discharging Status
| ClusterSOC | ClusterSOC |  | Cluster SOC | 0x04 | 0x3007 | R0 | 0.001 | u16 | 0 to 1000 | System Power Display
| ClusterSOH | ClusterSOH |  | Cluster SOH | 0x04 | 0x3008 | R0 | 0.001 | u16 | 0 to 1000 |  |  | --
| Cluster绝缘值 | ClusterInsulation |  | Cluster Insulation Value | 0x04 | 0x3009 | R0 | KΩ | u16 | 0 to 65535 |  |  | --
| Cluster正极绝缘值 | ClusterPosInsulation |  | Cluster Positive Pole Insulation Value | 0x04 | 0x300A | R0 | KΩ | u16 | 0 to 65535 |  |  | --
| Cluster负极绝缘值 | ClusterNegInsulation |  | Cluster Negative Pole Insulation Value | 0x04 | 0x300B | R0 | KΩ | u16 | 0 to 65535 |  |  | --
| Cluster单体电压最高节序号 | ClusterMaxCellVoltID |  | Cluster Cell Voltage Highest Section Number | 0x04 | 0x300C | R0 | - | u16 | 1# to N# (N is the number of battery strings) |  |  | --
| Cluster单体最高电压值 | ClusterMaxCellVolt |  | Cluster Cell Voltage Highest Value | 0x04 | 0x300D | R0 | mV | u16 | 0 to 5000 |  |  | --
| Cluster单体电压最低节序号 | ClusterMinCellVolID |  | Cluster Cell Voltage Lowest Section Number | 0x04 | 0x300E | R0 | - | u16 | 1# to N# (N is the number of battery strings) |  |  | --
| Cluster单体最低电压值 | ClusterMinCellVolt |  | Cluster Cell Voltage Lowest Value | 0x04 | 0x300F | R0 | Mv | u16 | 0 to 5000 |  |  | --
| Cluster单体温度最高节序号 | ClusterMaxCellTempID |  | Cluster Cell Temperature Highest Section Number | 0x04 | 0x3010 | R0 | - | u16 | 1# to N# (N is the number of NTC strings) |  |  | --
| Cluster单体温度最高值 | ClusterMaxCellTemp |  | Cluster Cell Temperature Highest Value | 0x04 | 0x3011 | R0 | ℃ | s16 | −40 to 125 |  |  | --
| Cluster单体温度最低节序号 | ClusterMinCellTempID |  | Cluster Cell Temperature Lowest Section Number | 0x04 | 0x3012 | R0 | - | u16 | 1# to N# (N is the number of NTC strings) |  |  | --
| Cluster单体温度最低值 | ClusterMinCellTemp |  | Cluster Cell Temperature Lowest Value | 0x04 | 0x3013 | R0 | ℃ | s16 | −40 to 125 | Current total power of the battery cluster
| Cluster当前总功率 | ClusterPower |  | Cluster Current Total Power | 0x04 | 0x3014~0x3015 | R0 | Kw | int32 |  | --
| Cluster平均电压 | ClusterAverageVolt |  | Cluster Average Voltage | 0x04 | 0x3016 | R0 | mV | u16 | 0 to 5000 | --
| Cluster平均温度 | ClusterAverageTemp |  | Cluster Average Temperature | 0x04 | 0x3017 | R0 | ℃ | u16 | −40 to 125 | --
| ClusterPDU温度1 | ClusterPDUTemp1 |  | Cluster PDU Temperature 1 | 0x04 | 0x3018 | R0 | ℃ | u16 | −40 to 125 | --
| ClusterPDU温度2 | ClusterPDUTemp2 |  | Cluster PDU Temperature 2 | 0x04 | 0x3019 | R0 | ℃ | u16 | −40 to 125 | --
| Cluster可放电量 |  |  | Cluster Dischargeable Capacity | 0x04 | 0x301A | R0 | Ah | u16
| Cluster可充电量 |  |  | Cluster Chargeable Capacity | 0x04 | 0x301B | R0 | Ah | u16
| Cluster充电限流 |  |  | Cluster Charge Current Limit | 0x04 | 0x301C | R0 | A | u16 |  | Battery Cluster Current Current/Charging Current Limit
| Cluster放电限流 |  |  | Cluster Discharge Current Limit | 0x04 | 0x301D | R0 | A | u16 |  | Battery Cluster Current Current/Discharging Current Limit
| Cluster充电限功率 |  |  | Cluster Charge Power Limit | 0x04 | 0x301E | R0 | Kw | u16 |  | Battery Cluster Total Current Power/Charging Power Limit
| Cluster放电限功率 |  |  | Cluster Discharge Power Limit | 0x04 | 0x301F | R0 | KW | u16 |  | Battery Cluster Total Current Power/Discharging Power Limit
| Cluster累计充电电量 |  |  | Cluster Cumulative Charged Energy | 0x04 | 0x3020~0x2021 | R0 | MWh | u16
| Cluster累计放电电量 |  |  | Cluster Cumulative Discharged Energy | 0x04 | 0x3022~0x2023 | R0 | MWh | u16
| Cluster充放电循环次数 |  |  | Cluster Charge/Discharge Cycle Count | 0x04 | 0x3024 | R0 |  | u16
| Cluster单次充电电量 |  |  |  | 0x04 | 0x3025~0x3026 | R0 | Kwh | u16
| 8 |  |  |  | 0x04 | 0x3027~0x3028 | R0 | Kwh | u16
| ClusterPDU温度3 | ClusterPDUTemp1 |  |  | 0x04 | 0x3029 | R0 | ℃ | u16 | −40 to 125
| ClusterPDU温度4 | ClusterPDUTemp2 |  |  | 0x04 | 0x302A | R0 | ℃ | u16 | −40 to 125
| BMS版本号1 |  |  |  | 0x04 | 0x302B | R0 |  | u16
| BMS版本号2 |  |  |  | 0x04 | 0x302C | R0 |  | u16
| BMS版本号3 |  |  |  | 0x04 | 0x302D | R0 |  | u16
预留
| Cluster故障码 | ClusterErrorCode |  |  | 0x04 | 0x30C0~0x30FF | R0 |  | U16 | Directly Forward Cluster Fault Code | Reserved 64 fault types, storing cluster faults, with a maximum capacity of 64 faults |  | --
CLUSTER_DATA(Battery cell information)
| Cluster单体均衡状态 | BcuCellVolt[1] ~ BcuCellVolt[512] |  |  | 0x02 | 0x3100 ~ 0x32FF | R0 | - | - | 0 to 511, one Cell Voltage Balancing Status per address |  |  | --
| Cluster单体电池电压 | BcuCellVolt[1] ~ BcuCellVolt[512] |  |  | 0x04 | 0x3300 ~ 0x34FF | R0 | Mv | u16 | 0 to 511, one Cell Voltage per address | Request via address pointer Equilibrium state requested via discrete quantities |  | --
| Cluster单体电池温度 | BcuCellTemp[1] ~ BcuCellTemp[512] |  |  | 0x04 | 0x3500 ~ 0x35FF | R0 | ℃ | u16 | 0 to 511, two Cell Temperatures per address, |  |  | --
STACK_DATA(Stack data): (Display according to the stack, stack view, stack summary data)
| Data reading example | Rx:01 04 36 00 00 23 BE 5B Tx:01 04 46 00 04 22 B8 FF 04 00 01 03 E8 03 E7 FF FE 00 7A FF FE 00 16 00 F8 0D E3 00 03 00 17 0C 96 00 42 00 21 00 4D 00 02 00 19 00 42 1A 0A 00 40 00 00 04 E7 00 00 04 F1 00 90 00 9B 00 00 04 D1 00 00 04 DC 00 02 00 21 15 81
| 当前Stack状态 | StackWorkingmode |  | Stack Current Status | 0x04 | 0x3600 | R0 | - | u16 | 0: Normal (Rack can discharge, can charge); 1: Charge Prohibited (Rack can discharge, cannot charge); 2: Discharge Prohibited (Rack can charge, cannot discharge); 3: Standby (Rack cannot charge or discharge); 4: Shutdown (Rack cannot charge or discharge); 5: Alarm (Rack cannot charge, simultaneously Charge Prohibited and Discharge Prohibited) 6: Fault (Rack cannot charge, simultaneously main positive and main negative contactors are open) 0xAA: No Communication |  |  | 簇2级BMS(电池）显示； 全部位“0：时，结合“系统级BMS(电池）”状态显示；若发生簇告警，则状态灯中的其中1-2个显示告警即可。正常时，结合系统状态显示
| Stack电池总电压 | StackTotalVolt |  | Stack Total Battery Voltage | 0x04 | 0x3601 | R0 | 0.1V | u16 |  |  |  | --
| Stack电池总电流 | StackTotalCurrent |  | Stack Total Battery Current | 0x04 | 0x3602 | R0 | 0.1A | s16 | Charging current is negative, discharging is positive | Current of Battery Cluster
| Stack充放电指示 | StackChgorDChgState |  | Stack Charge/Discharge Indication | 0x04 | 0x3603 | R0 | - | u16 | 0x0: Static; 0x1: Discharging; 0x2: Charging | Battery Charging/Discharging Status
| StackSOC | StackSOC |  | Stack SOC | 0x04 | 0x3604 | R0 | 0.001 | u16 | 0 to 1000 | System Power Display
| StackSOH | StackSOH |  | Stack SOH | 0x04 | 0x3605 | R0 | 0.001 | u16 | 0 to 1000 |  |  | --
| Stack绝缘值 | StackInsulation |  | Stack Insulation Value | 0x04 | 0x3606 | R0 | KΩ | u16 | 0 to 65535 |  |  | --
| Stack正极绝缘值 | StackPosInsulation |  | Stack Positive Pole Insulation Value | 0x04 | 0x3607 | R0 | KΩ | u16 | 0 to 65535 |  |  | --
| Stack负极绝缘值 | StackNegInsulation |  | Stack Negative Pole Insulation Value | 0x04 | 0x3608 | R0 | KΩ | u16 | 0 to 65535 |  |  | --
| Stack单体电压最高节簇号 | StackMaxCellVoltID |  | Stack Cell Voltage Highest Cluster Number | 0x04 | 0x3609 | R0 | - | u16 | 1# to N# (N is the number of battery clusters) |  |  | --
| Stack单体电压最高节串号 | StacClusterkMaxCellVoltID |  | Stack Cell Voltage Highest String Number | 0x04 | 0x360A | R0 | - | u16 | 1# to N# (N is the total number of single-cluster voltages) |  |  | --
| Stack单体最高电压值 | StackMaxCellVolt |  | Stack Cell Voltage Highest Value | 0x04 | 0x360B | R0 | mV | u16 | 0 to 5000 |  |  | --
| Stack单体电压最低节簇号 | StackMinCellVolID |  | Stack Cell Voltage Lowest Cluster Number | 0x04 | 0x360C | R0 | - | u16 | 1# to N# (N is the number of battery clusters) |  |  | --
| Stack单体电压最低节串号 | StackClusterMinCellVolID |  | Stack Cell Voltage Lowest String Number | 0x04 | 0x360D | R0 | - | u16 | 1# to N# (N is the total number of single-cluster voltages) |  |  | --
| Stack单体最低电压值 | StackMinCellVolt |  | Stack Cell Voltage Lowest Value | 0x04 | 0x360E | R0 | Mv | u16 | 0 to 5000 |  |  | --
| Stack单体温度最高节簇号 | StackMaxCellTempID |  | Stack Cell Temperature Highest Cluster Number | 0x04 | 0x360F | R0 | - | u16 | 1# to N# (N is the number of battery clusters) |  |  | --
| Stack单体温度最高节串号 | StackClusterMaxCellTempID |  | Stack Cell Temperature Highest String Number | 0x04 | 0x3610 | R0 | - | s16 | 1# to N# (N is the total number of single-cluster temperature sensors) |  |  | --
| Stack单体温度最高值 | StackMaxCellTemp |  | Stack Cell Temperature Highest Value | 0x04 | 0x3611 | R0 | ℃ | s16 | −40 to 125 |  |  | --
| Stack单体温度最低节簇号 | StackMinCellTempID |  | Stack Cell Temperature Lowest Cluster Number | 0x04 | 0x3612 | R0 | - | u16 | 1# to N# (N is the number of battery clusters) |  |  | --
| Stack单体温度最低节串号 | StackClusterMinCellTempID |  | Stack Cell Temperature Lowest String Number | 0x04 | 0x3613 | R0 | - | u16 | 1# to N# (N is the total number of single-cluster temperature sensors) |  |  | --
| Stack单体温度最低值 | StackMinCellTemp |  | Stack Cell Temperature Lowest Value | 0x04 | 0x3614 | R0 | ℃ | s16 | −40 to 125 |  |  | --
| Stack平均电压 | StackAverageVolt |  | Stack Average Voltage | 0x04 | 0x3615 | R0 | mV | u16 | 0 to 5000 |  |  | --
| Stack平均温度 | StackAverageTemp |  | Stack Average Temperature | 0x04 | 0x3616 | R0 | ℃ | s16 | −40 to 125 |  |  | --
| Stack可放电量 | StackDchgCap |  | Stack Dischargeable Capacity | 0x04 | 0x3617~0x3618 | R0 | 0.1kWh | u32 | 0 to 4,294,967,29.5 | Total Discharge Energy Display
| Stack可充电量 | StackChgCap |  | Stack Chargeable Capacity | 0x04 | 0x3619~0x361A | R0 | 0.1kWh | u32 | 0 to 4,294,967,29.5 | Total Charge Energy Display
| Stack充电限流 | StackChgLImit |  | Stack Charge Current Limit | 0x04 | 0x361B | R0 | 0.1A | s16 | Charging current is negative, discharging is positive | Battery Stack Total Current / Battery Stack Charge Current Limit
| Stack放电限流 | StackDChgLImit |  | Stack Discharge Current Limit | 0x04 | 0x361C | R0 | 0.1A | s16 | Charging current is negative, discharging is positive | Battery Stack Total Current / Battery Stack Discharge Current Limit
| Stack充电限功率 | StackChgPowerLImit |  | Stack Charge Power Limit | 0x04 | 0x361D~0x361E | R0 | 0.01 KW | int32 | Charging is negative, discharging is positive | Battery Stack Total Power / Battery Stack Charge Power Limit
| Stack放电限功率 | StackDChgPowerLImit |  | Stack Discharge Power Limit | 0x04 | 0x361F~0x3620 | R0 | 0.01 KW | int32 | Charging is negative, discharging is positive | Battery Stack Total Power / Battery Stack Discharge Power Limit
| StackPDU温度1 | StackPDUTemp1 |  | Stack PDU Temperature 1 | 0x04 | 0x3621 | R0 | ℃ | u16 | −40 to 125 |  |  | --
| StackPDU温度2 | StackPDUTemp2 |  | Stack PDU Temperature 2 | 0x04 | 0x3622 | R0 | ℃ | u16 | −40 to 125 |  |  | --
| StackPDU温度3 | StackPDUTemp3 |  | Stack PDU Temperature 3 | 0x04 | 0x3623 | R0 | ℃ | u16 | −40 to 125 |  |  | --
| StackPDU温度4 | StackPDUTemp4 |  | Stack PDU Temperature 4 | 0x04 | 0x3624 | R0 | ℃ | u16 | −40 to 125 |  |  | --
| Stack电池总功率 |  |  | Stack Total Battery Power | 0x04 | 0x3625~0x3626 | R0 | 0.01 KW | int32 | Charging is negative, discharging is positive
| Stack当前并簇方式 |  |  | Stack Current Parallel Cluster Mode | 0x04 | 0x3627 | R0 |  | u16 | 0 - Invalid; 1 - Highest voltage cluster first; 2 - Lowest voltage cluster first
| Stack最少允许并簇数 |  |  | Stack Minimum Allowed Parallel Clusters | 0x04 | 0x3628 | R0 |  | u16 | 1 to 16
| Stack并簇压差 |  |  | Stack Parallel Cluster Voltage Difference | 0x04 | 0x3629 | R0 | 1V | u16 | 0 to 100V
| Stack需要充电均衡状态 |  |  | Stack Charge Balancing Status Required | 0x04 | 0x362A | R0 |  | u16 | 0 - Invalid; 1 - Balancing required; 2 - Balancing not required
| Stack并簇状态 |  |  | Stack Parallel Cluster Status | 0x04 | 0x362B | R0 |  | u16 | 0 - Normal Operation (Actual Parallel Cluster Count = Full Cluster Count) 1 - Minor Cluster Under-Run (Minimum Parallel Cluster Count < Actual Parallel Cluster Count < Full Cluster Count) 2 - Moderate Cluster Under-Run (0< Actual Parallel Cluster Count < Minimum Parallel Cluster Count) 3 - Severe Cluster Under-Run (Actual Parallel Cluster Count = 0)
| 本堆下簇１状态 |  |  | Status of Cluster 1 in this Stack | 0x04 | 0x362C | R0 |  | u16 | 0 - Not Paralleled (Main positive and main negative contactors are open) 1 - Paralleled (Main positive and main negative contactors are closed)
| 本堆下簇２状态 |  |  | Status of Cluster 2 in this Stack | 0x04 | 0x362D | R0 |  | u16
| 本堆下簇３状态 |  |  | Status of Cluster 3 in this Stack | 0x04 | 0x362E | R0 |  | u16
| 本堆下簇４状态 |  |  | Status of Cluster 4 in this Stack | 0x04 | 0x362F | R0 |  | u16
| 本堆下簇５状态 |  |  | Status of Cluster 5 in this Stack | 0x04 | 0x3630 | R0 |  | u16
| 本堆下簇６状态 |  |  | Status of Cluster 6 in this Stack | 0x04 | 0x3631 | R0 |  | u16
| 本堆下簇７状态 |  |  | Status of Cluster 7 in this Stack | 0x04 | 0x3632 | R0 |  | u16
| 本堆下簇８状态 |  |  | Status of Cluster 8 in this Stack | 0x04 | 0x3633 | R0 |  | u16
| 本堆下簇９状态 |  |  | Status of Cluster 9 in this Stack | 0x04 | 0x3634 | R0 |  | u16
| 本堆下簇１０状态 |  |  | Status of Cluster 10 in this Stack | 0x04 | 0x3635 | R0 |  | u16
| 本堆下簇１１状态 |  |  | Status of Cluster 11 in this Stack | 0x04 | 0x3636 | R0 |  | u16
| 本堆下簇１２状态 |  |  | Status of Cluster 12 in this Stack | 0x04 | 0x3637 | R0 |  | u16
| 本堆下簇１３状态 |  |  | Status of Cluster 13 in this Stack | 0x04 | 0x3638 | R0 |  | u16
| 本堆下簇１４状态 |  |  | Status of Cluster 14 in this Stack | 0x04 | 0x3639 | R0 |  | u16
| 本堆下簇１５状态 |  |  | Status of Cluster 15 in this Stack | 0x04 | 0x363A | R0 |  | u16
| 预留 |  |  | Reserved
| 本堆下簇１状态 |  |  | Status of Cluster 1 in this Stack | 0x04 | 0x3650 | R0 |  | u16 | 0: Normal (Rack can discharge, can charge); 1: Charge Prohibited (Rack can discharge, cannot charge); 2: Discharge Prohibited (Rack can charge, cannot discharge); 3: Standby (Rack cannot charge or discharge); 4: Shutdown (Rack cannot charge or discharge); 0xAA: No Communication
| 本堆下簇２状态 |  |  | Status of Cluster 2 in this Stack | 0x04 | 0x3651 | R0 |  | u16
| 本堆下簇３状态 |  |  | Status of Cluster 3 in this Stack | 0x04 | 0x3652 | R0 |  | u16
| 本堆下簇４状态 |  |  | Status of Cluster 4 in this Stack | 0x04 | 0x3653 | R0 |  | u16
| 本堆下簇５状态 |  |  | Status of Cluster 5 in this Stack | 0x04 | 0x3654 | R0 |  | u16
| 本堆下簇６状态 |  |  | Status of Cluster 6 in this Stack | 0x04 | 0x3655 | R0 |  | u16
| 本堆下簇７状态 |  |  | Status of Cluster 7 in this Stack | 0x04 | 0x3656 | R0 |  | u16
| 本堆下簇８状态 |  |  | Status of Cluster 8 in this Stack | 0x04 | 0x3657 | R0 |  | u16
| 本堆下簇９状态 |  |  | Status of Cluster 9 in this Stack | 0x04 | 0x3658 | R0 |  | u16
| 本堆下簇１０状态 |  |  | Status of Cluster 10 in this Stack | 0x04 | 0x3659 | R0 |  | u16
| 本堆下簇１１状态 |  |  | Status of Cluster 11 in this Stack | 0x04 | 0x365A | R0 |  | u16
| 本堆下簇１２状态 |  |  | Status of Cluster 12 in this Stack | 0x04 | 0x365B | R0 |  | u16
| 本堆下簇１３状态 |  |  | Status of Cluster 13 in this Stack | 0x04 | 0x365C | R0 |  | u16
| 本堆下簇１４状态 |  |  | Status of Cluster 14 in this Stack | 0x04 | 0x365D | R0 |  | u16
| 本堆下簇１５状态 |  |  | Status of Cluster 15 in this Stack | 0x04 | 0x365E | R0 |  | u16
| 本堆下簇１６状态 |  |  | Status of Cluster 16 in this Stack | 0x04 | 0x365F | R0 |  | u16
| 本堆下簇１~16簇 SOC |  |  | SOC of Clusters 1-16 in this Stack | 0x04 | 0x3660~0x366F | R0 |  | u16 | Each address represents a cluster, with a precision of 0.1, where 1000 represents 100%
| 本堆下簇１~16簇 SOH |  |  | SOH of Clusters 1-16 in this Stack | 0x04 | 0x3670~0x367F | R0 |  | u16 | Each address represents a cluster, with a precision of 0.1, where 1000 represents 100%
| 本堆下簇１~16簇 电压 |  |  | Voltage of Clusters 1-16 in this Stack | 0x04 | 0x3680~0x368F | R0 |  | u16 | Each address represents a cluster, with a precision of 0.1, where 1000 represents 100V
| 本堆下簇１~16簇 电流 |  |  | Current of Clusters 1-16 in this Stack | 0x04 | 0x3690~0x369F | R0 |  | s16 | Each address represents a cluster, with a precision of 0.1, where 1000 represents 100A
--
| Stack故障 | StackFaultInfo |  | Stack Fault | 0x04 | 0x36C0~0x36FF | R0 |  | U16 | Directly Forward Stack Fault Code | Reserved 64 fault types for storing PCS faults, with a maximum capacity of 64 faults |  | --
PACK_DATA：
| pack1最高温度 |  |  | Pack 1 Maximum Temperature |  | 0x3030 | R0 |  |  | ‘-40~125
| pack1最高温度位置 |  |  | Pack 1 Maximum Temperature Location |  | 0x3031 | R0
| pack1最低温度 |  |  | Pack 1 Minimum Temperature |  | 0x3032 | R0 |  |  | ‘-40~125
| pack1最低温度位置 |  |  | Pack 1 Minimum Temperature Location |  | 0x3033 | R0
| pack1最高电压 |  |  | Pack 1 Maximum Voltage |  | 0x3034 | R0 |  |  | 0~5000
| pack1最高电压位置 |  |  | Pack 1 Maximum Voltage Location |  | 0x3035 | R0
| pack1最低电压 |  |  | Pack 1 Minimum Voltage |  | 0x3036 | R0 |  |  | 0~5000
| pack1最低电压位置 |  |  | Pack 1 Minimum Voltage Location |  | 0x3037 | R0
| pack1正极极柱温度 |  |  | Pack 1 Positive Terminal Temperature |  | 0x3038 | R0 |  |  | ‘-40~125
| pack1负极极柱温度 |  |  | Pack 1 Negative Terminal Temperature |  | 0x3039 | R0 |  |  | ‘-40~125
| pack2最高温度 |  |  | Pack 2 Maximum Temperature |  | 0x303A | R0 |  |  | ‘-40~125
| pack2最高温度位置 |  |  | Pack 2 Maximum Temperature Location |  | 0x303B | R0
| pack2最低温度 |  |  | Pack 2 Minimum Temperature |  | 0x303C | R0 |  |  | ‘-40~125
| pack2最低温度位置 |  |  | Pack 2 Minimum Temperature Location |  | 0x303D | R0
| pack2最高电压 |  |  | Pack 2 Maximum Voltage |  | 0x303E | R0 |  |  | 0~5000
| pack2最高电压位置 |  |  | Pack 2 Maximum Voltage Location |  | 0x303F | R0
| pack2最低电压 |  |  | Pack 2 Minimum Voltage |  | 0x3040 | R0 |  |  | 0~5000
| pack2最低电压位置 |  |  | Pack 2 Minimum Voltage Location |  | 0x3041 | R0
| pack2正极极柱温度 |  |  | Pack 2 Positive Terminal Temperature |  | 0x3042 | R0 |  |  | ‘-40~125
| pack2负极极柱温度 |  |  | Pack 2 Negative Terminal Temperature |  | 0x3043 | R0 |  |  | ‘-40~125
| pack3最高温度 |  |  | Pack 3 Maximum Temperature |  | 0x3044 | R0 |  |  | ‘-40~125
| pack3最高温度位置 |  |  | Pack 3 Maximum Temperature Location |  | 0x3045 | R0
| pack3最低温度 |  |  | Pack 3 Minimum Temperature |  | 0x3046 | R0 |  |  | ‘-40~125
| pack3最低温度位置 |  |  | Pack 3 Minimum Temperature Location |  | 0x3047 | R0
| pack3最高电压 |  |  | Pack 3 Maximum Voltage |  | 0x3048 | R0 |  |  | 0~5000
| pack3最高电压位置 |  |  | Pack 3 Maximum Voltage Location |  | 0x3049 | R0
| pack3最低电压 |  |  | Pack 3 Minimum Voltage |  | 0x304A | R0 |  |  | 0~5000
| pack3最低电压位置 |  |  | Pack 3 Minimum Voltage Location |  | 0x304B | R0
| pack3正极极柱温度 |  |  | Pack 3 Positive Terminal Temperature |  | 0x304C | R0 |  |  | ‘-40~125
| pack3负极极柱温度 |  |  | Pack 3 Negative Terminal Temperature |  | 0x304D | R0 |  |  | ‘-40~125
| pack4最高温度 |  |  | Pack 4 Maximum Temperature |  | 0x304E | R0 |  |  | ‘-40~125
| pack4最高温度位置 |  |  | Pack 4 Maximum Temperature Location |  | 0x304F | R0
| pack4最低温度 |  |  | Pack 4 Minimum Temperature |  | 0x3050 | R0 |  |  | ‘-40~125
| pack4最低温度位置 |  |  | Pack 4 Minimum Temperature Location |  | 0x3051 | R0
| pack4最高电压 |  |  | Pack 4 Maximum Voltage |  | 0x3052 | R0 |  |  | 0~5000
| pack4最高电压位置 |  |  | Pack 4 Maximum Voltage Location |  | 0x3053 | R0
| pack4最低电压 |  |  | Pack 4 Minimum Voltage |  | 0x3054 | R0 |  |  | 0~5000
| pack4最低电压位置 |  |  | Pack 4 Minimum Voltage Location |  | 0x3055 | R0
| pack4正极极柱温度 |  |  | Pack 4 Positive Terminal Temperature |  | 0x3056 | R0 |  |  | ‘-40~125
| pack4负极极柱温度 |  |  | Pack 4 Negative Terminal Temperature |  | 0x3057 | R0 |  |  | ‘-40~125
| pack5最高温度 |  |  | Pack 5 Maximum Temperature |  | 0x3058 | R0 |  |  | ‘-40~125
| pack5最高温度位置 |  |  | Pack 5 Maximum Temperature Location |  | 0x3059 | R0
| pack5最低温度 |  |  | Pack 5 Minimum Temperature |  | 0x305A | R0 |  |  | ‘-40~125
| pack5最低温度位置 |  |  | Pack 5 Minimum Temperature Location |  | 0x305B | R0
| pack5最高电压 |  |  | Pack 5 Maximum Voltage |  | 0x305C | R0 |  |  | 0~5000
| pack5最高电压位置 |  |  | Pack 5 Maximum Voltage Location |  | 0x305D | R0
| pack5最低电压 |  |  | Pack 5 Minimum Voltage |  | 0x305E | R0 |  |  | 0~5000
| pack5最低电压位置 |  |  | Pack 5 Minimum Voltage Location |  | 0x305F | R0
| pack5正极极柱温度 |  |  | Pack 5 Positive Terminal Temperature |  | 0x3070 | R0 |  |  | ‘-40~125
| pack5负极极柱温度 |  |  | Pack 5 Negative Terminal Temperature |  | 0x3061 | R0 |  |  | ‘-40~125
| pack6最高温度 |  |  | Pack 6 Maximum Temperature |  | 0x3062 | R0 |  |  | ‘-40~125
| pack6最高温度位置 |  |  | Pack 6 Maximum Temperature Location |  | 0x3063 | R0
| pack6最低温度 |  |  | Pack 6 Minimum Temperature |  | 0x3064 | R0 |  |  | ‘-40~125
| pack6最低温度位置 |  |  | Pack 6 Minimum Temperature Location |  | 0x3065 | R0
| pack6最高电压 |  |  | Pack 6 Maximum Voltage |  | 0x3066 | R0 |  |  | 0~5000
| pack6最高电压位置 |  |  | Pack 6 Maximum Voltage Location |  | 0x3067 | R0
| pack6最低电压 |  |  | Pack 6 Minimum Voltage |  | 0x3068 | R0 |  |  | 0~5000
| pack6最低电压位置 |  |  | Pack 6 Minimum Voltage Location |  | 0x3069 | R0
| pack6正极极柱温度 |  |  | Pack 6 Positive Terminal Temperature |  | 0x306A | R0 |  |  | ‘-40~125
| pack6负极极柱温度 |  |  | Pack 6 Negative Terminal Temperature |  | 0x306B | R0 |  |  | ‘-40~125
| pack7最高温度 |  |  | Pack 7 Maximum Temperature |  | 0x306C | R0 |  |  | ‘-40~125
| pack7最高温度位置 |  |  | Pack 7 Maximum Temperature Location |  | 0x306D | R0
| pack7最低温度 |  |  | Pack 7 Minimum Temperature |  | 0x306E | R0 |  |  | ‘-40~125
| pack7最低温度位置 |  |  | Pack 7 Minimum Temperature Location |  | 0x306F | R0
| pack7最高电压 |  |  | Pack 7 Maximum Voltage |  | 0x3070 | R0 |  |  | 0~5000
| pack7最高电压位置 |  |  | Pack 7 Maximum Voltage Location |  | 0x3071 | R0
| pack7最低电压 |  |  | Pack 7 Minimum Voltage |  | 0x3072 | R0 |  |  | 0~5000
| pack7最低电压位置 |  |  | Pack 7 Minimum Voltage Location |  | 0x3073 | R0
| pack7正极极柱温度 |  |  | Pack 7 Positive Terminal Temperature |  | 0x3074 | R0 |  |  | ‘-40~125
| pack7负极极柱温度 |  |  | Pack 7 Negative Terminal Temperature |  | 0x3075 | R0 |  |  | ‘-40~125
| pack8最高温度 |  |  | Pack 8 Maximum Temperature |  | 0x3076 | R0 |  |  | ‘-40~125
| pack8最高温度位置 |  |  | Pack 8 Maximum Temperature Location |  | 0x3077 | R0
| pack8最低温度 |  |  | Pack 8 Minimum Temperature |  | 0x3078 | R0 |  |  | ‘-40~125
| pack8最低温度位置 |  |  | Pack 8 Minimum Temperature Location |  | 0x3079 | R0
| pack8最高电压 |  |  | Pack 8 Maximum Voltage |  | 0x307A | R0 |  |  | 0~5000
| pack8最高电压位置 |  |  | Pack 8 Maximum Voltage Location |  | 0x307B | R0
| pack8最低电压 |  |  | Pack 8 Minimum Voltage |  | 0x307C | R0 |  |  | 0~5000
| pack8最低电压位置 |  |  | Pack 8 Minimum Voltage Location |  | 0x307D | R0
| pack8正极极柱温度 |  |  | Pack 8 Positive Terminal Temperature |  | 0x307E | R0 |  |  | ‘-40~125
| pack8负极极柱温度 |  |  | Pack 8 Negative Terminal Temperature |  | 0x307F | R0 |  |  | ‘-40~125
AIR_DATA
| Data reading example | Rx:01 04 3A 01 00 1D 6D 1B Tx:01 04 3A 00 07 00 03 00 00 00 01 00 01 FF F5 00 DE 00 00 02 58 00 DE 00 01 80 00 02 62 02 8A 7F FF 00 41 FF FF 00 FF 02 9A 03 78 03 09 02 9A FF FF FF FF 02 9A 00 00 00 00 0D 05 01 4D 10 93
| 空调运行状态运行状态 | AirWorkingmode |  | AC Unit Running Status | 0x04 | 0x3A01 | R0 | / | u16 | XQ |  |  | --
| 室内风机状态 | AirInFanState |  | Indoor Fan Status | 0x04 | 0x3A02 | R0 | / | u16 | 0: Stop, 1: Start, 3: Not Selected |  |  | --
| 室外风机状态 | AirOutFanState |  | Outdoor Fan Status | 0x04 | 0x3A03 | R0 | / | u16 | 0: Stop, 1: Start, 3: Not Selected |  |  | --
| 压缩机状态 | AirCompressorState |  | Compressor Status | 0x04 | 0x3A04 | R0 | / | u16 | 0: Stop, 1: Start, 3: Not Selected |  |  | --
| 电加热运行状态 | AirPTC_State |  | Electric Heater Running Status | 0x04 | 0x3A05 | R0 | / | u16 | 0: Stop, 1: Start, 3: Not Selected |  |  | --
| 柜内温度 | AirTemp |  | Cabinet Internal Temperature | 0x04 | 0x3A06 | R0 | 0.1℃ | u16 | 0: Stop, 1: Start, 3: Not SelectedTemperature offset 40,−40 to 125 |  |  | --
| 柜内湿度 | AirHum |  | Cabinet Internal Humidity | 0x04 | 0x3A07 | R0 | 0.1% | u16 |  |  |  | --
| 储能系统温差 | AirSystemTempDiff |  | Energy Storage System Temperature Difference | 0x04 | 0x3A08 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 柜外温度 | AirOutTemp |  | Cabinet External Temperature | 0x04 | 0x3A09 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 出风温度 | AirOutPutTemp |  | Air Outlet Temperature | 0x04 | 0x3A0A | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 应急风机状态 | AirEmergencyFanState |  | Emergency Fan Status | 0x04 | 0x3A0B | R0 |  | u16 | 0: Stop, 1: Start, 3: Not Selected |  |  | --
| 盘管温度 | AirCoiltemperature |  | Coil Temperature | 0x04 | 0x3A0C | R0 | 0.1℃ | u16 | 0: Stop, 1: Start, 3: Not SelectedTemperature offset 40,−40 to 125 |  |  | --
| 冷凝温度 | AirCondensationTemperature |  | Condensing Temperature | 0x04 | 0x3A0D | R0 | 0.1℃ | u16 | 0: Stop, 1: Start, 3: Not SelectedTemperature offset 40,−40 to 125 |  |  | --
| 融霜湿度 | AirHumidity |  | Defrosting Humidity | 0x04 | 0x3A0E | R0 | 0.1% | u16 |  |  |  | --
| 排气温度 | AirExhaustTemperature |  | Exhaust Temperature | 0x04 | 0x3A0F | R0 | 0.1℃ | u16 | 0: Stop, 1: Start, 3: Not SelectedTemperature offset 40,−40 to 125 |  |  | --
| 电流 | AirCurrent |  | Current | 0x04 | 0x3A10 | R0 | 0.1A | S16 |  |  |  | --
| 交流电压 | AirACVoltage |  | AC Voltage | 0x04 | 0x3A11 | R0 | 0.1V | u16 |  |  |  | --
| 直流电压 | AirDCVoltage |  | DC Voltage | 0x04 | 0x3A12 | R0 | 0.1V | u16 |  |  |  | --
| 制冷点 | AirCoolOnPoint |  | Cooling Setpoint | 0x04 | 0x3A13 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 制冷禁止点 | AirCoolOffPoint |  | Cooling Inhibit Setpoint | 0x04 | 0x3A14 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 加热点 | AirHeatOnPoint |  | Heating Setpoint | 0x04 | 0x3A15 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 加热禁止点 | AirHeatOffPoint |  | Heating Inhibit Setpoint | 0x04 | 0x3A16 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 高温报警点 | AirHighTempPoint |  | High Temperature Alarm Setpoint | 0x04 | 0x3A17 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 高温报警解除点 | AirHighTempReturn |  | High Temperature Alarm Release Setpoint | 0x04 | 0x3A18 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 低温点报警点 | AirLowTempPoint |  | Low Temperature Alarm Setpoint | 0x04 | 0x3A19 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 低温报警解除点 | AirLowTempReturn |  | Low Temperature Alarm Release Setpoint | 0x04 | 0x3A1A | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 高湿点 | AirHumidityPoint |  | High Humidity Setpoint | 0x04 | 0x3A1B | R0 | 0.1% | u16 |  |  |  | --
| 内风机停止点 | AirInternalFanPoint |  | Internal Fan Stop Setpoint | 0x04 | 0x3A1C | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 融霜温度 | AirDefrostTemp |  | Defrosting Temperature | 0x04 | 0x3A1D | R0 | 0.1℃ | u16 | 0: Stop, 1: Start, 3: Not SelectedTemperature offset 40,−40 to 125 |  |  | --
| 预留 | 预留 |  | Reserved | 预留 | [7 empty] | --
--
| 风扇1转速 | Fan1RPM |  | Fan 1 Speed | 0x04 | 0x3A40 | R0 | RPM | u16 |  |  |  | --
| 风扇2转速 | Fan2RPM |  | Fan 2 Speed | 0x04 | 0x3A41 | R0 | RPM | u16 |  |  |  | --
| 风扇3转速 | Fan3RPM |  | Fan 3 Speed | 0x04 | 0x3A42 | R0 | RPM | u16 |  |  |  | --
| 风扇4转速 | Fan4RPM |  | Fan 4 Speed | 0x04 | 0x3A43 | R0 | RPM | u16 |  |  |  | --
| 风扇5转速 | Fan5RPM |  | Fan 5 Speed | 0x04 | 0x3A44 | R0 | RPM | u16 |  |  |  | --
| 风扇6转速 | Fan6RPM |  | Fan 6 Speed | 0x04 | 0x3A45 | R0 | RPM | u16 |  |  |  | --
| 风扇7转速 | Fan7RPM |  | Fan 7 Speed | 0x04 | 0x3A46 | R0 | RPM | u16 |  |  |  | --
| 风扇8转速 | Fan8RPM |  | Fan 8 Speed | 0x04 | 0x3A47 | R0 | RPM | u16 |  |  |  | --
| 风扇1开启温度 | Fan1OnTemperature |  | Fan 1 Start-up Temperature | 0x04 | 0x3A48 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇2开启温度 | Fan2OnTemperature |  | Fan 2 Start-up Temperature | 0x04 | 0x3A49 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇3开启温度 | Fan3OnTemperature |  | Fan 3 Start-up Temperature | 0x04 | 0x3A4A | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇4开启温度 | Fan4OnTemperature |  | Fan 4 Start-up Temperature | 0x04 | 0x3A4B | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇5开启温度 | Fan5OnTemperature |  | Fan 5 Start-up Temperature | 0x04 | 0x3A4C | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇6开启温度 | Fan6OnTemperature |  | Fan 6 Start-up Temperature | 0x04 | 0x3A4D | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇7开启温度 | Fan7OnTemperature |  | Fan 7 Start-up Temperature | 0x04 | 0x3A4E | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇8开启温度 | Fan8OnTemperature |  | Fan 8 Start-up Temperature | 0x04 | 0x3A4F | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇1关闭温度 | Fan1OffTemperature |  | Fan 1 Shut-down Temperature | 0x04 | 0x3A50 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇2关闭温度 | Fan2OffTemperature |  | Fan 2 Shut-down Temperature | 0x04 | 0x3A51 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇3关闭温度 | Fan3OffTemperature |  | Fan 3 Shut-down Temperature | 0x04 | 0x3A52 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇4关闭温度 | Fan4OffTemperature |  | Fan 4 Shut-down Temperature | 0x04 | 0x3A53 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇5关闭温度 | Fan5OffTemperature |  | Fan 5 Shut-down Temperature | 0x04 | 0x3A54 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇6关闭温度 | Fan6OffTemperature |  | Fan 6 Shut-down Temperature | 0x04 | 0x3A55 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇7关闭温度 | Fan7OffTemperature |  | Fan 7 Shut-down Temperature | 0x04 | 0x3A56 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇8关闭温度 | Fan8OffTemperature |  | Fan 8 Shut-down Temperature | 0x04 | 0x3A57 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 风扇状态 | FANState |  | Fan Status | 0x04 | 0x3A58 | R0 |  | u16 | 0 - Shutdown; 1 - Running; 2 - Fault; 0xAA: No Communication
| TM1温度 | TM1Temperature |  | TM1 Temperature | 0x04 | 0x3A59 | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| TM2温度 | TM2Temperature |  | TM2 Temperature | 0x04 | 0x3A5A | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| TM3温度 | TM3Temperature |  | TM3 Temperature | 0x04 | 0x3A5B | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| TM4温度 | TM4Temperature |  | TM4 Temperature | 0x04 | 0x3A5C | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| TM5温度 | TM5Temperature |  | TM5 Temperature | 0x04 | 0x3A5D | R0 | 0.1℃ | u16 | Temperature offset 40 |  |  | --
| 预留 | 预留 |  | Reserved | 预留 | [7 empty] | --
| 风扇报警 | AirFaultInfo |  | Fan Alarm | 0x04 | 0x3A80~0x3ABF | R0 |  | u16 | Directly Forward Fan Fault Code | Reserved 64 fault types for storing Cluster faults, with a maximum capacity of 64 faults |  | --
| 空调报警 | AirFaultInfo |  | AC Alarm | 0x04 | 0x3AC0~0x3AFF | R0 |  | u16 | Directly Forward Fan Fault Code | Reserved 64 fault types for storing Cluster faults, with a maximum capacity of 64 faults |  | Associated with one system indicator light. When the AC Unit or Liquid Cooling Unit fails, this light flashes for alarm.
--
--
门禁状态（待定） | [12 empty] | --
| 通信状态 | DoorComState |  | Communication Status | 0x04 | 0x3E00 | R0 |  | u16 | 0 - Reserved; 1 - Normal; 2 - No Communication |  |  | --
| 门禁开关状态 | DoorRunState |  | Access Control Switch Status | 0x04 | 0x3E01 | R0 |  | u16 | 0 - Reserved; 1 - Open Status; 2 - Closed Status; |  |  | One of the associated system indicator lights (access control) flashes as an alarm when the door is opened; under normal conditions, it remains steadily lit according to the system status.
| 门禁报警等级 | DoorAlarmLevel |  | Access Control Alarm Level | 0x04 | 0x3E02 | R0 |  | u16 | 0 - No Alarm; 1 - Level 1 Alarm; 2 - Level 2 Alarm; 3 - Level 3 Alarm; |  |  | --
--
| 预留状态 |  |  | Reserved Status | [8 empty] | --
| 门禁报警 | DoorFaultInfo |  | Access Control Alarm | 0x04 | 0x3EC0~0x3EFF | R0 |  | u16 | Directly Forward Access Control Fault Code | Reserved 64 fault types for storing Cluster faults, with a maximum capacity of 64 faults |  | --
消防状态（待定）
| 通信状态 | FireComState |  | Communication Status | 0x04 | 0x4000 | R0 |  | u16 | 0-预留； 1-正常； 2-无通信
总状态 | 运行状态 | FireRunState |  | Running Status | 0x04 | 0x4001 | R0 |  | u16 | 0-预留；1-正常；2-异常； |  |  | One of the linked system indicator lights (fire protection) flashes as an alarm when abnormal; it remains steadily lit when normal.
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4002 | R0 | 1ppm | u16 |  |  |  | --
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4003 | R0 | 1ppm | u16 |  |  |  | --
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4004 | R0 | 0.1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4005 | R0 | 1ppm | u16 |  |  |  | --
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4006 | R0 | 1ppm | u16 |  |  |  | --
| 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4007 | R0 |  | u16 | 0-Reserved; 1-Level 1 alarm; 2-Level 2 alarm; 3-Level 3 alarm; 4-Level 4 alarm; 5-No fault |  |  | One of the linked system indicator lights (fire protection) flashes as an alarm when abnormal; it remains steadily lit when normal.
| CO浓度报警 | COAlarm |  | CO Concentration Alarm | 0x04 | 0x4008 | R0 | 1ppm | u16 | 0-Reserved; 1-Level 1 alarm; 2-Level 2 alarm; 3-Level 3 alarm; 4-Level 4 alarm; 5-No fault |  |  | --
| 氢气浓度报警 | H2Alarm |  | Hydrogen Concentration Alarm | 0x04 | 0x4009 | R0 | 1ppm | u16 | 0-Reserved; 1-Level 1 alarm; 2-Level 2 alarm; 3-Level 3 alarm; 4-Level 4 alarm; 5-No fault |  |  | --
| 烟雾报警 | SomgAlarm |  | Smoke Alarm | 0x04 | 0x400A | R0 | 0.1℃ | u16 | 0-Reserved; 1-Level 1 alarm; 2-Level 2 alarm; 3-Level 3 alarm; 4-Level 4 alarm; 5-No fault |  |  | --
| 高温报警 | TempAlarm |  | High Temperature Alarm | 0x04 | 0x400B | R0 | 1ppm | u16 | 0-Reserved; 1-Level 1 alarm; 2-Level 2 alarm; 3-Level 3 alarm; 4-Level 4 alarm; 5-No fault |  |  | --
| VOC报警 | TVOCAlarm |  | VOC Alarm | 0x04 | 0x400C | R0 | 1ppm | u16 | 0-Reserved; 1-Level 1 alarm; 2-Level 2 alarm; 3-Level 3 alarm; 4-Level 4 alarm; 5-No fault |  |  | --
| 水浸报警 | WaterAlarm |  | Water Immersion Alarm | 0x04 | 0x400D | R0 |  | u16 | 0-Reserved; 1-Level 1 alarm; 2-Level 2 alarm; 3-Level 3 alarm; 4-Level 4 alarm; 5-No fault |  |  | --
探头1 | 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4010
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4011 |  | 1ppm |  | Display the numerical value only
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4012 |  | 1ppm |  | Display the numerical value only
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4013 |  | 0.1℃ |  | Temperature offset 40, -40~125
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4014 |  | 1ppm |  | Display the numerical value only
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4015 |  | 1ppm |  | Display the numerical value only
| 故障类型 |  |  | Fault Type | 0x04 | 0x4016 |  |  |  | Display the numerical value only
| 启动类型 |  |  | Startup Type | 0x04 | 0x4017 |  |  |  | Display the numerical value only
| 子阀门状态（喷头状态） |  |  | Sub-valve Status (Sprinkler Status) | 0x04 | 0x4018 |  |  |  | Display the numerical value only
探头2 | 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4020
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4021 |  | 1ppm |  | Display the numerical value only
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4022 |  | 1ppm |  | Display the numerical value only
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4023 |  | 0.1℃ |  | Temperature offset 40, -40~125
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4024 |  | 1ppm |  | Display the numerical value only
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4025 |  | 1ppm |  | Display the numerical value only
| 故障类型 |  |  | Fault Type | 0x04 | 0x4026 |  |  |  | Display the numerical value only
| 启动类型 |  |  | Startup Type | 0x04 | 0x4027 |  |  |  | Display the numerical value only
| 子阀门状态（喷头状态） |  |  | Sub-valve Status (Sprinkler Status) | 0x04 | 0x4028 |  |  |  | Display the numerical value only
探头3 | 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4030
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4031 |  | 1ppm |  | Display the numerical value only
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4032 |  | 1ppm |  | Display the numerical value only
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4033 |  | 0.1℃ |  | Temperature offset 40, -40~125
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4034 |  | 1ppm |  | Display the numerical value only
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4035 |  | 1ppm |  | Display the numerical value only
| 故障类型 |  |  | Fault Type | 0x04 | 0x4036 |  |  |  | Display the numerical value only
| 启动类型 |  |  | Startup Type | 0x04 | 0x4037 |  |  |  | Display the numerical value only
| 子阀门状态（喷头状态） |  |  | Sub-valve Status (Sprinkler Status) | 0x04 | 0x4038 |  |  |  | Display the numerical value only
探头4 | 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4040
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4041 |  | 1ppm |  | Display the numerical value only
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4042 |  | 1ppm |  | Display the numerical value only
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4043 |  | 0.1℃ |  | Temperature offset 40, -40~125
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4044 |  | 1ppm |  | Display the numerical value only
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4045 |  | 1ppm |  | Display the numerical value only
| 故障类型 |  |  | Fault Type | 0x04 | 0x4046 |  |  |  | Display the numerical value only
| 启动类型 |  |  | Startup Type | 0x04 | 0x4047 |  |  |  | Display the numerical value only
| 子阀门状态（喷头状态） |  |  | Sub-valve Status (Sprinkler Status) | 0x04 | 0x4048 |  |  |  | Display the numerical value only
探头5 | 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4050
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4051 |  | 1ppm |  | Display the numerical value only
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4052 |  | 1ppm |  | Display the numerical value only
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4053 |  | 0.1℃ |  | Temperature offset 40, -40~125
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4054 |  | 1ppm |  | Display the numerical value only
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4055 |  | 1ppm |  | Display the numerical value only
| 故障类型 |  |  | Fault Type | 0x04 | 0x4056 |  |  |  | Display the numerical value only
| 启动类型 |  |  | Startup Type | 0x04 | 0x4057 |  |  |  | Display the numerical value only
| 子阀门状态（喷头状态） |  |  | Sub-valve Status (Sprinkler Status) | 0x04 | 0x4058 |  |  |  | Display the numerical value only
探头6 | 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4060
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4061 |  | 1ppm |  | Display the numerical value only
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4062 |  | 1ppm |  | Display the numerical value only
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4063 |  | 0.1℃ |  | Temperature offset 40, -40~125
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4064 |  | 1ppm |  | Display the numerical value only
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4065 |  | 1ppm |  | Display the numerical value only
| 故障类型 |  |  | Fault Type | 0x04 | 0x4066 |  |  |  | Display the numerical value only
| 启动类型 |  |  | Startup Type | 0x04 | 0x4067 |  |  |  | Display the numerical value only
| 子阀门状态（喷头状态） |  |  | Sub-valve Status (Sprinkler Status) | 0x04 | 0x4068 |  |  |  | Display the numerical value only
探头7 | 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4070
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4071 |  |  |  | Display the numerical value only
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4072 |  | 1ppm |  | Display the numerical value only
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4073 |  | 1ppm |  | Temperature offset 40, -40~125
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4074 |  | 0.1℃ |  | Display the numerical value only
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4075 |  | 1ppm |  | Display the numerical value only
| 故障类型 |  |  | Fault Type | 0x04 | 0x4076 |  | 1ppm |  | Display the numerical value only
| 启动类型 |  |  | Startup Type | 0x04 | 0x4077 |  |  |  | Display the numerical value only
| 子阀门状态（喷头状态） |  |  | Sub-valve Status (Sprinkler Status) | 0x04 | 0x4078 |  |  |  | Display the numerical value only
探头8 | 报警等级 | AlarmLevel |  | Alarm Level | 0x04 | 0x4080
| CO浓度 | COState |  | CO Concentration | 0x04 | 0x4081 |  |  |  | Display the numerical value only
| 氢气浓度 | H2State |  | Hydrogen Concentration | 0x04 | 0x4082 |  |  |  | Display the numerical value only
| 温度数值 | FireTemperature |  | Temperature Value | 0x04 | 0x4083 |  |  |  | Temperature offset 40, -40~125
| 烟雾数值 | SomgState |  | Smoke Value | 0x04 | 0x4084 |  |  |  | Display the numerical value only
| VOC数值 | TVOCState |  | VOC Value | 0x04 | 0x4085 |  |  |  | Display the numerical value only
| 故障类型 |  |  | Fault Type | 0x04 | 0x4086 |  |  |  | Display the numerical value only
| 启动类型 |  |  | Startup Type | 0x04 | 0x4087 |  |  |  | Display the numerical value only
| 子阀门状态（喷头状态） |  |  | Sub-valve Status (Sprinkler Status) | 0x04 | 0x4088 |  |  |  | Display the numerical value only
--
| 消防故障码 | FireFaultInfo |  | Firefighting Fault Code | 0x04 | 0x40C0~0x40FF | R0 |  | u16 | Forward the fire alarm fault code directly | Reserve 64 U16 fault types for storing cluster faults, with a maximum capacity of 64 faults. |  | --
液冷（TMS）状态（待定）
| Data reading example | Rx:01 04 41 00 00 0D 25 F3 Tx:01 04 1A 00 04 00 03 00 02 00 FF 00 3E 00 3F 00 40 00 55 00 42 00 FF 02 9A 00 FF 03 57 37 BD
| 运行状态 | TMSComState |  | Running Status | 0x04 | 0x4100 | R0 |  | u16 | 0-Idle; 1-Ready to start; 2-Running; 3-Delayed shutdown; 4-Fault; 0xAA: No communication | Cannot receive TMS message reporting no communication, TMS may be sending messages but is in a shutdown state. |  | One of the associated system indicator lights flashes as an alarm when there is a fault in the air conditioning or liquid cooling unit; it remains steadily lit when no abnormalities are present.
| 运行模式 | TMSRunState |  | Operating Mode | 0x04 | 0x4101 | R0 |  | u16 | 0-Reserved; 1-Cooling Mode; 2-Heating Mode; 3-Recirculation Mode; 4-Auto Mode; |  |  | --
| 报警状态 | TMSAlarm |  | Alarm Status | 0x04 | 0x4102 | R0 |  | u16 | 0-Reserved; 1-Level 1 alarm; 2-Level 2 alarm; 3-Level 3 alarm; 4-Level 4 alarm; 5-No fault |  |  | --
| 供液温度（液体从TMS出去） | TMSSupplyTemperature |  | Supply Fluid Temperature (Fluid exiting TMS) | 0x04 | 0x4103 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 回液温度（液体回到TMS） | TMSReturnTemperature |  | Return Fluid Temperature (Fluid returning to TMS) | 0x04 | 0x4104 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 制冷开启温度 | StartCoolTemp |  | Cooling Start Temperature | 0x04 | 0x4105 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 制冷关闭温度 | StopCoolTemp |  | Cooling Stop Temperature | 0x04 | 0x4106 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 制热开启温度 | StartHeatTemp |  | Heating Start Temperature | 0x04 | 0x4107 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 制热关闭温度 | StartHeatTemp |  | Heating Stop Temperature | 0x04 | 0x4108 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 环境温度 | EnvirTemp |  | Ambient Temperature | 0x04 | 0x4109 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 供液压力（液体从TMS出去） | InPortPressure |  | Supply Fluid Pressure (Fluid exiting TMS) | 0x04 | 0x410A | R0 | 0.1bar | u16 |  |  |  | --
| 回液压力（液体回到TMS） | OutPortPressure |  | Return Fluid Pressure (Fluid returning to TMS) | 0x04 | 0x410B | R0 | 0.1℃ | u16 |  |  |  | --
| TMS恒温方式预设温度 | TMSConstantTemperaturePresettemperature |  | TMS Constant Temperature Preset | 0x04 | 0x410C | R0 |  | u16 | Temperature offset 40, -40~125 |  |  | --
| 吸气温度 |  |  | Suction Temperature | 0x04 | 0x410D | R0 | 0.1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 板换温度 |  |  | Plate Heat Exchanger Temperature | 0x04 | 0x410E | R0 | 0.1℃ | u16 | Temperature offset 40, -40~125
| 冷凝盘管温度 |  |  | Condenser Coil Temperature | 0x04 | 0x410F | R0 | 0.1℃ | u16 | Temperature offset 40, -40~125
| 进出水压差值 |  |  | Inlet/Outlet Water Pressure Difference | 0x04 | 0x4110 | R0 | 0.1bar | u16
| 高压侧压力值 |  |  | High-Side Pressure | 0x04 | 0x4111 | R0 | 0.1bar | u16
| 低压侧压力值 |  |  | Low-Side Pressure | 0x04 | 0x4112 | R0 | 0.1bar | u16
| 电子膨胀阀开度 |  |  | Electronic Expansion Valve Opening | 0x04 | 0x4113 | R0 |  | u16
| 交流供电电压 |  |  | AC Supply Voltage | 0x04 | 0x4114 | R0 | 0.1V | u16
| 压缩机转速 |  |  | Compressor Speed | 0x04 | 0x4115 | R0 |  | u16
| 系统流量 |  |  | System Flow Rate | 0x04 | 0x4116 | R0 |  | u16
| 排气温度 |  |  | Exhaust Temperature | 0x04 | 0x4117 | R0 | 0.1℃ | u16 | Temperature offset 40, -40~125
| 水泵转速 |  |  | Water Pump Speed | 0x04 | 0x4118 | R0 |  | u16
| 2#吸气温度 |  |  | 2# Suction Temperature | 0x04 | 0x4119 | R0 | 0.1℃ | u16 | Temperature offset 40, -40~125
| 2#高压侧压力值 |  |  | 2# High-Side Pressure | 0x04 | 0x411A | R0 | 0.1bar | u16
| 2#低压侧压力值 |  |  | 2# Low-Side Pressure | 0x04 | 0x411B | R0 | 0.1bar | u16
| 2#电子膨胀阀开度 |  |  | 2# Electronic Expansion Valve Opening | 0x04 | 0x411C | R0 |  | u16
| 2#压缩机转速 |  |  | 2# Compressor Speed | 0x04 | 0x411D | R0 |  | u16
| 2#排气温度 |  |  | 2# Exhaust Temperature | 0x04 | 0x411E | R0 | 0.1℃ | u16 | Temperature offset 40, -40~125
| 2#水泵转速 |  |  | 2# Water Pump Speed | 0x04 | 0x411F | R0 |  | u16
| TMS补液--补液泵手动模式 |  |  | TMS Refill - Refill Pump Manual Mode | 0x04 | 0x4120 | R0 |  | u16 | 0-Reserved: 1-Closed:2-Open
| TMS补液--补液泵手动状态 |  |  | TMS Refill - Refill Pump Manual Status | 0x04 | 0x4121 | R0 |  | u16 | 0-Reserved: 1-Closed:2-Open
| 补液桶液位状态 |  |  | Refill Tank Fluid Level Status | 0x04 | 0x4122 | R0 |  | u16 | 0-Reserved: 1-Normal:2-Abnormal;255-Unused
| TMS故障码 | TMSFaultInfo |  |  | 0x04 | 0x41C0~0x41FF | R0 |  | u16 | 直接转发TMS的故障码 | Reserve 64 U16 fault types for storing cluster faults, with a maximum capacity of 64 faults. |  | One of the associated system indicator lights flashes an alarm when there is a fault in the air conditioning or liquid cooling unit; it remains lit normally according to the system status.
外设（待定） | [12 empty] | --
--
| Data reading example | Rx:01 04 42 00 00 07 A5 B0 Tx:01 04 0E 00 01 00 01 00 01 00 01 00 01 00 01 00 00 DA 0A Rx:01 04 42 80 00 07 A4 58 Tx:01 04 0E 00 01 00 01 00 01 00 01 00 01 00 01 00 00 DA 0A
| 急停触发 |  |  | Emergency Stop Triggered | 0x04 | 0x4200 | R0 |  | u16 | 0-Normal; 1: Emergency stop fault |  |  | One of the associated system indicator lights flashes an alarm when triggered; it remains lit normally according to the system status.
| 消防触发 |  |  | Firefighting Triggered | 0x04 | 0x4201 | R0 |  | u16 | 0-Normal; 1: Fire triggered |  |  | One of the associated system indicator lights (fire protection) flashes an alarm when triggered; it remains lit normally according to the system status.
| 温感触发 |  |  | Temperature Sensor Triggered | 0x04 | 0x4202 | R0 |  | u16 | 0-Normal; 1: Temperature anomaly |  |  | One of the associated system indicator lights (fire protection) flashes an alarm when triggered; it remains lit normally according to the system status.
| 门禁触发 |  |  | Access Control Triggered | 0x04 | 0x4203 | R0 |  | u16 | 0-Door closed; 1: Door open
| 水浸触发 |  |  | Water Immersion Triggered | 0x04 | 0x4204 | R0 |  | u16 | 0-Normal; 1: Water leakage fault
| 烟感触发 |  |  | Smoke Sensor Triggered | 0x04 | 0x4205 | R0 |  | u16 | 0-Normal; 1: Smoke alarm
| 交流断路器状态（交流输入检测） |  |  | AC Breaker Status (AC Input Detection) | 0x04 | 0x4206 | R0 |  | u16 | 0-Disconnected; 1: Closed
| 消防喷洒触发 |  |  | Fire Suppression Sprinkler Triggered | 0x04 | 0x4207 | R0 |  | u16 | 0-Normal; 1-Abnormal
| 消防故障触发 |  |  | Firefighting Fault Triggered | 0x04 | 0x4208 | R0 |  | u16 | 0-Normal; 1-Abnormal
| DC防雷触发 |  |  | DC Lightning Protection Triggered | 0x04 | 0x4209 | R0 |  | u16 | 0-Normal; 1-Abnormal
| AC防雷触发 |  |  | AC Lightning Protection Triggered | 0x04 | 0x420A | R0 |  | u16 | 0-Normal; 1-Abnormal
| PCS触发 |  |  | PCS Triggered | 0x04 | 0x420B | R0 |  | u16 | 0-Normal; 1-Abnormal
| 水流信号 |  |  | Water Flow Signal | 0x04 | 0x420C | R0 |  | u16 | 0-Normal; 1-Abnormal
| 电池MSD信号 |  |  | Battery MSD Signal | 0x04 | 0x420D | R0 |  | u16 | 0-Normal; 1-Abnormal
| HDI1 |  |  |  | 0x04 | 0x420E | R0 |  | u16 | 0-Normal; 1-Abnormal
| HDI2 |  |  |  | 0x04 | 0x420F | R0 |  | u16 | 0-Normal; 1-Abnormal
| HDI3 |  |  |  | 0x04 | 0x4210 | R0 |  | u16 | 0-Normal; 1-Abnormal
| HDI4 |  |  |  | 0x04 | 0x4211 | R0 |  | u16 | 0-Normal; 1-Abnormal
| LDI1 |  |  |  | 0x04 | 0x4212 | R0 |  | u16 | 0-Normal; 1-Abnormal
| LDI2 |  |  |  | 0x04 | 0x4213 | R0 |  | u16 | 0-Normal; 1-Abnormal
| LDI3 |  |  |  | 0x04 | 0x4214 | R0 |  | u16 | 0-Normal; 1-Abnormal
| LDI4 |  |  |  | 0x04 | 0x4215 | R0 |  | u16 | 0-Normal; 1-Abnormal
| HSD1 |  |  |  | 0x04 | 0x4216 | R0 |  | u16 | 0-Normal; 1-Abnormal
| HSD2 |  |  |  | 0x04 | 0x4217 | R0 |  | u16 | 0-Normal; 1-Abnormal
| HSD3 |  |  |  | 0x04 | 0x4218 | R0 |  | u16 | 0-Normal; 1-Abnormal
| HSD4 |  |  |  | 0x04 | 0x4219 | R0 |  | u16 | 0-Normal; 1-Abnormal
| LSD1 |  |  |  | 0x04 | 0x421A | R0 |  | u16 | 0-Normal; 1-Abnormal
| LSD2 |  |  |  | 0x04 | 0x421B | R0 |  | u16 | 0-Normal; 1-Abnormal
| LSD3 |  |  |  | 0x04 | 0x421C | R0 |  | u16 | 0-Normal; 1-Abnormal
| LSD4 |  |  |  | 0x04 | 0x421D | R0 |  | u16 | 0-Normal; 1-Abnormal
| DO1 |  |  |  | 0x04 | 0x421E | R0 |  | u16 | 0-Normal; 1-Abnormal
| DO2 |  |  |  | 0x04 | 0x421F | R0 |  | u16 | 0-Normal; 1-Abnormal
| DO3 |  |  |  | 0x04 | 0x4220 | R0 |  | u16 | 0-Normal; 1-Abnormal
| DO4 |  |  |  | 0x04 | 0x4221 | R0 |  | u16 | 0-Normal; 1-Abnormal
| DO5 |  |  |  | 0x04 | 0x4222 | R0 |  | u16 | 0-Normal; 1-Abnormal
| DO6 |  |  |  | 0x04 | 0x4223 | R0 |  | u16 | 0-Normal; 1-Abnormal
| DO7 |  |  |  | 0x04 | 0x4224 | R0 |  | u16 | 0-Normal; 1-Abnormal
| DO8 |  |  |  | 0x04 | 0x4225 | R0 |  | u16 | 0-Normal; 1-Abnormal
u16
| 急停使能 |  |  | Emergency Stop Enable | 0x04 | 0x4280 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | One of the associated system indicator lights (Access Control) flashes as an alarm when abnormal; when normal, it remains lit according to the system light.
| 消防使能 |  |  | Firefighting Enable | 0x04 | 0x4281 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | One of the associated system indicator lights (water immersion) flashes as an alarm when abnormal; when normal, it remains lit according to the system light.
| 温感使能 |  |  | Temperature Sensor Enable | 0x04 | 0x4282 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | One of the associated system indicator lights (firefighting) flashes as an alarm when abnormal; when normal, it remains lit according to the system light.
| 门禁使能 |  |  | Access Control Enable | 0x04 | 0x4283 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | --
| 水浸使能 |  |  | Water Immersion Enable | 0x04 | 0x4284 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | --
| 烟感使能 |  |  | Smoke Sensor Enable | 0x04 | 0x4285 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | --
| 交流断路器状态使能 |  |  | AC Breaker Status Enable | 0x04 | 0x4286 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | --
| 消防喷洒使能 |  |  | Fire Suppression Sprinkler Enable | 0x04 | 0x4287 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | --
| 消防故障使能 |  |  | Firefighting Fault Enable | 0x04 | 0x4288 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | --
| DC防雷使能 |  |  | DC Lightning Protection Enable | 0x04 | 0x4289 | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | --
| AC防雷使能 |  |  | AC Lightning Protection Enable | 0x04 | 0x428A | R0 |  | u16 | 0-Disabled; 1: Enabled |  |  | --
| PCS使能 |  |  | PCS Enable | 0x04 | 0x428B | R0 |  | u16 | 0-Disabled; 1: Enabled
| 水流信号使能 |  |  | Water Flow Signal Enable | 0x04 | 0x428C | R0 |  | u16 | 0-Disabled; 1: Enabled
| 电池MSD信号使能 |  |  | Battery MSD Signal Enable | 0x04 | 0x428D | R0 |  | u16 | 0-Disabled; 1: Enabled
| HDI1 |  |  |  | 0x04 | 0x428E | R0 |  | u16 | 0-Disabled; 1: Enabled
| HDI2 |  |  |  | 0x04 | 0x428F | R0 |  | u16 | 0-Disabled; 1: Enabled
| HDI3 |  |  |  | 0x04 | 0x4290 | R0 |  | u16 | 0-Disabled; 1: Enabled
| HDI4 |  |  |  | 0x04 | 0x4291 | R0 |  | u16 | 0-Disabled; 1: Enabled
| LDI1 |  |  |  | 0x04 | 0x4292 | R0 |  | u16 | 0-Disabled; 1: Enabled
| LDI2 |  |  |  | 0x04 | 0x4293 | R0 |  | u16 | 0-Disabled; 1: Enabled
| LDI3 |  |  |  | 0x04 | 0x4294 | R0 |  | u16 | 0-Disabled; 1: Enabled
| LDI4 |  |  |  | 0x04 | 0x4295 | R0 |  | u16 | 0-Disabled; 1: Enabled
| HSD1 |  |  |  | 0x04 | 0x4296 | R0 |  | u16 | 0-Disabled; 1: Enabled
| HSD2 |  |  |  | 0x04 | 0x4297 | R0 |  | u16 | 0-Disabled; 1: Enabled
| HSD3 |  |  |  | 0x04 | 0x4298 | R0 |  | u16 | 0-Disabled; 1: Enabled
| HSD4 |  |  |  | 0x04 | 0x4299 | R0 |  | u16 | 0-Disabled; 1: Enabled
| LSD1 |  |  |  | 0x04 | 0x429A | R0 |  | u16 | 0-Disabled; 1: Enabled
| LSD2 |  |  |  | 0x04 | 0x429B | R0 |  | u16 | 0-Disabled; 1: Enabled
| LSD3 |  |  |  | 0x04 | 0x429C | R0 |  | u16 | 0-Disabled; 1: Enabled
| LSD4 |  |  |  | 0x04 | 0x429D | R0 |  | u16 | 0-Disabled; 1: Enabled
| DO1 |  |  |  | 0x04 | 0x429E | R0 |  | u16 | 0-Disabled; 1: Enabled
| DO2 |  |  |  | 0x04 | 0x429F | R0 |  | u16 | 0-Disabled; 1: Enabled
| DO3 |  |  |  | 0x04 | 0x42A0 | R0 |  | u16 | 0-Disabled; 1: Enabled
| DO4 |  |  |  | 0x04 | 0x42A1 | R0 |  | u16 | 0-Disabled; 1: Enabled
| DO5 |  |  |  | 0x04 | 0x42A2 | R0 |  | u16 | 0-Disabled; 1: Enabled
| DO6 |  |  |  | 0x04 | 0x42A3 | R0 |  | u16 | 0-Disabled; 1: Enabled
| DO7 |  |  |  | 0x04 | 0x42A4 | R0 |  | u16 | 0-Disabled; 1: Enabled
| DO8 |  |  |  | 0x04 | 0x42A5 | R0 |  | u16 | 0-Disabled; 1: Enabled
--
Dehumidifier | [12 empty] | --
--
| Data reading example | Rx:01 04 43 00 00 0A 65 89 Tx:01 04 14 00 01 00 41 00 46 00 37 00 37 00 32 00 37 00 2D 00 00 00 00 06 6C
| 除湿器运行状态 |  |  | Dehumidifier Running Status | 0x04 | 0x4300 | R0 |  | u16 | 0-Reserved; 1-Normal (Humidity Control); 2-Abnormal; 3-Stop; AA-Communication Abnormal |  |  | One of the associated system indicator lights (dehumidifier) flashes as an alarm when abnormal; when normal, it remains lit according to the system light.
| 除湿器室内温度 |  |  | Dehumidifier Indoor Temperature | 0x04 | 0x4301 | R0 |  | u16 | Temperature offset 40, -40~125 |  |  | --
| 除湿器室外温度 |  |  | Dehumidifier Outdoor Temperature | 0x04 | 0x4302 | R0 |  | u16 | Temperature offset 40, -40~125 |  |  | --
| 除湿器湿度 |  |  | Dehumidifier Humidity | 0x04 | 0x4303 | R0 |  | u16 | 1% |  |  | --
| 除湿温度启动值 |  |  | Dehumidification Start Temperature | 0x04 | 0x4304 | R0 |  | u16 | Temperature offset 40, -40~125 |  |  | --
| 除湿温度断开值 |  |  | Dehumidification Stop Temperature | 0x04 | 0x4305 | R0 |  | u16 | Temperature offset 40, -40~125 |  |  | --
| 除湿湿度启动值 |  |  | Dehumidification Start Humidity | 0x04 | 0x4306 | R0 |  | u16 | 1% |  |  | --
| 除湿湿度断开值 |  |  | Dehumidification Stop Humidity | 0x04 | 0x4307 | R0 |  | u16 | 1% |  |  | --
| 温度传感器故障 |  |  | Temperature Sensor Fault | 0x04 | 0x4308 | R0 |  | u16 | 0-正常；1：故障（0-Normal 1-Abnormal） |  |  | --
| 湿度传感器故障 |  |  | Humidity Sensor Fault | 0x04 | 0x4309 | R0 |  | u16 | 0-正常；1：故障（0-Normal 1-Abnormal） |  |  | --
UPS | [12 empty] | --
--
| Data reading example | Rx:01 04 44 00 00 03 A4 FB Tx:01 04 06 00 01 00 01 00 00 0C 93 Rx:01 04 44 20 00 07 A4 F2 Tx:01 04 0E 00 00 00 4C 00 6F 1D 89 00 42 02 2B 00 7B BF 85
| UPS运行状态 |  |  | UPS Running Status | 0x04 | 0x4400 | R0 |  | u16 | 0-预留；1-正常；2-异常；（0-Preserved;1-working;2-fault） |  |  | One of the associated system indicator lights (power) flashes as an alarm when abnormal; when normal, it remains lit according to the system light.
| UPS工作状态 |  |  | UPS Working Status | 0x04 | 0x4401 | R0 |  | u16 | UPS status: 0=预留 Preserved 1=POWE ON 上电状态 2=STANDBY 待机状态 3=BYPASS 旁路状态 4=LINE 市电工作状态 5=BAT 电池供电状态 6=TEST 测试自检放电状态 7=FAULT 故障状态 8=CONVERTER 9=HE 经济状态，基本等同于BYPASS 10=SHUTDOWN 关机状态 |  |  | --
| R相输入电压 | PcsVoltAB |  | R-phase Input Voltage | 0x04 | 0x4402~ 0x4403 | R0 | 0.01V | int32 |  |  |  | --
| S相输入电压 | PcsVoltBC |  | S-phase Input Voltage | 0x04 | 0x4404~ 0x4405 | R0 | 0.01V | int32 |  |  |  | --
| T相输入电压 | PcsVoltCA |  | T-phase Input Voltage | 0x04 | 0x4406~ 0x4407 | R0 | 0.01V | int32 |  |  |  | --
| R相输入电流 | PcsCurrentA |  | R-phase Input Current | 0x04 | 0x4408~ 0x4409 | R0 | 0.01A | int32 | ‘-3000 ~ 3000A |  |  | --
| S相输入电流 | PcsCurrentB |  | S-phase Input Current | 0x04 | 0x440A~ 0x440B | R0 | 0.01A | int32 | ‘-3000 ~ 3000A |  |  | --
| T相输入电流 | PcsCurrentC |  | T-phase Input Current | 0x04 | 0x440C~ 0x440D | R0 | 0.01A | int32 | ‘-3000 ~ 3000A |  |  | --
| 预留 | 预留 |  | Reserved | 0x04 | 0x440F | R0 | 预留 | 预留 | Preserved |  |  | --
| R相输出电压 | PcsVoltAB |  | R-phase Output Voltage | 0x04 | 0x4412~ 0x4413 | R0 | 0.01V | int32 |  |  |  | --
| S相输出电压 | PcsVoltBC |  | S-phase Output Voltage | 0x04 | 0x4414~ 0x4415 | R0 | 0.01V | int32 |  |  |  | --
| T相输出电压 | PcsVoltCA |  | T-phase Output Voltage | 0x04 | 0x4416~ 0x4417 | R0 | 0.01V | int32 |  |  |  | --
| R相输出电流 | PcsCurrentA |  | R-phase Output Current | 0x04 | 0x4418~ 0x4419 | R0 | 0.01A | int32 | ‘-3000 ~ 3000A |  |  | --
| S相输出电流 | PcsCurrentB |  | S-phase Output Current | 0x04 | 0x441A~ 0x441B | R0 | 0.01A | int32 | ‘-3000 ~ 3000A |  |  | --
| T相输出电流 | PcsCurrentC |  | T-phase Output Current | 0x04 | 0x441C~ 0x441D | R0 | 0.01A | int32 | ‘-3000 ~ 3000A |  |  | --
| 预留 | 预留 |  | Reserved | 0x04 | 0x441F | R0 | 预留 | 预留 | 预留 |  |  | --
| UPS类型 |  |  | UPS Type | 0x04 | 0x4420 | R0 |  |  | UPS类型: 0=ONLINE,1=BAKCUP |  |  | --
| UPS温度 |  |  | UPS Temperature | 0x04 | 0x4421 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 电池维持时间 |  |  | Battery Runtime | 0x04 | 0x4422 | R0 |  | u16 |  |  |  | --
| 直流电池总压 |  |  | DC Total Battery Voltage | 0x04 | 0x4423 | R0 | 0.1 V | u16 |  |  |  | --
| 直流电池温度 |  |  | DC Battery Temperature | 0x04 | 0x4424 | R0 | 1℃ | u16 | Temperature offset 40, -40~125 |  |  | --
| 直流电池容量SOC |  |  | DC Battery Capacity SOC | 0x04 | 0x4425 | R0 | 0.1% | u16 |  |  |  | --
| 直流电池电流 |  |  | DC Battery Current | 0x04 | 0x4426 | R0 | 0.1 A | u16 |  |  |  | --
| 额定总功率 |  |  | Rated Total Power | 0x04 | 0x4427 | R0 | 0.1 kW | u16 |  |  |  | --
| 额定输入电压种类 |  |  | Rated Input Voltage Type | 0x04 | 0x4428 | R0 |  | u16 |  |  |  | --
| 输出定额电压 |  |  | Rated Output Voltage | 0x04 | 0x4429 | R0 | 0.1 V | u16 |  |  |  | --
| 输出定额频率 |  |  | Rated Output Frequency | 0x04 | 0x442A | R0 | HZ | u16 |  |  |  | --
| 输入输出相数 |  |  | Input/Output Phase Count | 0x04 | 0x442B | R0 |  | u16 |  |  |  | --
| 额定电池电压 |  |  | Rated Battery Voltage | 0x04 | 0x442C | R0 | 0.1 V | u16 |  |  |  | --
| 输出定额电流 |  |  | Rated Output Current | 0x04 | 0x442D | R0 | 0.1 A | u16 |  |  |  | --
| 额定电池节数 |  |  | Rated Number of Battery Cells | 0x04 | 0x442F | R0 |  | u16 |  |  |  | --
实时故障(Bit 图查询 ，见离散量 ) Real-time Fault (Bit Map Query, see **Discrete Inputs**) | [12 empty] | --
| 0x1000~0x12FF ---簇故障码 Cluster Fault Code 0x1300~0x15FF ---堆故障码 Stack Fault Code 0x1600~0x18FF ---EMS故障码 EMS Fault Code 0x4200~0x4225---Peripheral (DI) Fault Code | Rx:01 02 10 00 00 40 7D 3A Tx:01 02 08 00 00 00 00 00 00 FF 01 44 22 Rx:01 02 11 00 00 40 7C C6 Tx:01 02 08 FF FF FF F7 FF FF 7F 00 45 D7 Rx:01 02 12 00 00 40 7C 82 Tx:01 02 08 FE FF FF FF FF FF FF 07 45 D8 | [10 empty] | As long as any device is abnormal, it corresponds to its respective indicator light.
历史故障 （0x5000~0x5FFF） 单次modbus传输252字节，126地址，可以发5条历史故障。 0x5000~0x5FFF，可发送32*5=160条故障，考虑情况是否拓展到0x6FFF~7FFF~8FFF等 Historical Faults (0x5000~0x5FFF) A single Modbus transmission can send bytes, corresponding to addresses, allowing for historical faults to be sent per transmission. The address range can store faults. You should consider expanding the address range to , , , etc., depending on the total number of historical faults you need to log and store.
| 索引号 |  |  | Index Number | 0x04 | 0x5000 | R0 |  |  | Count after each request to help fetch the next 5 pieces of data.
| 历史故障1 |  |  | Historical Fault 1 | 0x04 | 0x5001~0x5019 | R0 |  |  | Each historical fault occupies 50 bytes, | If it is a real-time fault, the end time is 00, and the time is recorded as milliseconds counted from 1970.
| 历史故障2 |  |  | Historical Fault 2 | 0x04 | 0x501A~0x5032 | R0 |  |  | Each historical fault occupies 50 bytes,
| 历史故障3 |  |  | Historical Fault 3 | 0x04 | 0x5033~0x504B | R0 |  |  | Each historical fault occupies 50 bytes,
| 历史故障4 |  |  | Historical Fault 4 | 0x04 | 0x504C~0x5064 | R0 |  |  | Each historical fault occupies 50 bytes,
| 历史故障5 |  |  | Historical Fault 5 | 0x04 | 0x5065~0x507D | R0 |  |  | Each historical fault occupies 50 bytes,

## HMI WRITE
Z
告警值 | [5 empty] | 告警响应时间 |  |  |  | 故障恢复值 |  |  |  |  | 恢复响应时间
单体过压一级告警值 | Cell Overvoltage Level 1 Alarm Value | 0x1900 | mV |  | Charge and Discharge Level 1 Alarms are both triggered. (Same for below) | 单体过压一级告警响应时间 | Cell Overvoltage Level 1 Alarm Response Time | 0x1940 |  | 单体过压一级恢复值 | Cell Overvoltage Level 1 Recovery Value | 0x1980 | mV |  | 单体过压一级恢复响应时间 | Cell Overvoltage Level 1 Recovery Response Time | 0x19C0
单体欠压一级告警值 | Cell Undervoltage Level 1 Alarm Value | 0x1901 | mV |  |  | 单体欠压一级告警响应时间 | Cell Undervoltage Level 1 Alarm Response Time | 0x1941 |  | 单体欠压一级恢复值 | Cell Undervoltage Level 1 Recovery Value | 0x1981 | mV |  | 单体欠压一级恢复响应时间 | Cell Undervoltage Level 1 Recovery Response Time | 0x19C1
总压过压一级告警值 | Total Voltage Overvoltage Level 1 Alarm Value | 0x1902 | 0.1V |  |  | 总压过压一级告警响应时间 | Total Voltage Overvoltage Level 1 Alarm Response Time | 0x1942 |  | 总压过压一级恢复值 | Total Voltage Overvoltage Level 1 Recovery Value | 0x1982 | 0.1V |  | 总压过压一级恢复响应时间 | Total Voltage Overvoltage Level 1 Recovery Response Time | 0x19C2
总压欠压一级告警值 | Total Voltage Undervoltage Level 1 Alarm Value | 0x1903 | 0.1V |  |  | 总压欠压一级告警响应时间 | Total Voltage Undervoltage Level 1 Alarm Response Time | 0x1943 |  | 总压欠压一级恢复值 | Total Voltage Undervoltage Level 1 Recovery Value | 0x1983 | 0.1V |  | 总压欠压一级恢复响应时间 | Total Voltage Undervoltage Level 1 Recovery Response Time | 0x19C3
单体压差一级告警值 | Cell Voltage Difference Level 1 Alarm Value | 0x1904 | mV |  |  | 单体压差一级告警响应时间 | Cell Voltage Difference Level 1 Alarm Response Time | 0x1944 |  | 单体压差一级恢复值 | Cell Voltage Difference Level 1 Recovery Value | 0x1984 | mV |  | 单体压差一级恢复响应时间 | Cell Voltage Difference Level 1 Recovery Response Time | 0x19C4
高压箱放电过流一级告警值 | High-Voltage Box Discharge Overcurrent Level 1 Alarm Value | 0x1905 | A |  |  | 高压箱放电过流一级告警响应时间 | High-Voltage Box Discharge Overcurrent Level 1 Alarm Response Time | 0x1945 |  | 高压箱放电过流一级恢复值 | High-Voltage Box Discharge Overcurrent Level 1 Recovery Value | 0x1985 | A |  | 高压箱放电过流一级恢复响应时间 | High-Voltage Box Discharge Overcurrent Level 1 Recovery Response Time | 0x19C5
充电过流一级告警值 | Charge Overcurrent Level 1 Alarm Value | 0x1906 | A |  |  | 充电过流一级告警响应时间 | Charge Overcurrent Level 1 Alarm Response Time | 0x1946 |  | 充电过流一级恢复值 | Charge Overcurrent Level 1 Recovery Value | 0x1986 | A |  | 充电过流一级恢复响应时间 | Charge Overcurrent Level 1 Recovery Response Time | 0x19C6
绝缘电阻一级告警值 | Insulation Resistance Level 1 Alarm Value | 0x1907 | Ω/V |  |  | 绝缘电阻一级告警响应时间 | Insulation Resistance Level 1 Alarm Response Time | 0x1947 |  | 绝缘电阻一级恢复值 | Insulation Resistance Level 1 Recovery Value | 0x1987 | Ω/V |  | 绝缘电阻一级恢复响应时间 | Insulation Resistance Level 1 Recovery Response Time | 0x19C7
充电高温一级告警值 | Charging High Temperature Level 1 Alarm Value | 0x1908 | ℃ | 50 ℃ Offset (Excluding Temperature Difference) |  | 充电高温一级告警响应时间 | Charging High Temperature Level 1 Alarm Response Time | 0x1948 |  | 充电高温一级恢复值 | Charging High Temperature Level 1 Recovery Value | 0x1988 | ℃ |  | 充电高温一级恢复响应时间 | Charging High Temperature Level 1 Recovery Response Time | 0x19C8
放电高温一级告警值 | Discharging High Temperature Level 1 Alarm Value | 0x1909 | ℃ |  |  | 放电高温一级告警响应时间 | Discharging High Temperature Level 1 Alarm Response Time | 0x1949 |  | 放电高温一级恢复值 | Discharging High Temperature Level 1 Recovery Value | 0x1989 | ℃ |  | 放电高温一级恢复响应时间 | Discharging High Temperature Level 1 Recovery Response Time | 0x19C9
充电低温一级告警值 | Charging Low Temperature Level 1 Alarm Value | 0x190A | ℃ |  |  | 充电低温一级告警响应时间 | Charging Low Temperature Level 1 Alarm Response Time | 0x194A |  | 充电低温一级恢复值 | Charging Low Temperature Level 1 Recovery Value | 0x198A | ℃ |  | 充电低温一级恢复响应时间 | Charging Low Temperature Level 1 Recovery Response Time | 0x19CA
放电低温一级告警值 | Discharging Low Temperature Level 1 Alarm Value | 0x190B | ℃ |  |  | 放电低温一级告警响应时间 | Discharging Low Temperature Level 1 Alarm Response Time | 0x194B |  | 放电低温一级恢复值 | Discharging Low Temperature Level 1 Recovery Value | 0x198B | ℃ |  | 放电低温一级恢复响应时间 | Discharging Low Temperature Level 1 Recovery Response Time | 0x19CB
温差过大一级告警值 | Excessive Temperature Difference Level 1 Alarm Value | 0x190C | ℃ |  |  | 温差过大一级告警响应时间 | Excessive Temperature Difference Level 1 Alarm Response Time | 0x194C |  | 温差过大一级恢复值 | Excessive Temperature Difference Level 1 Recovery Value | 0x198C | ℃ |  | 温差过大一级恢复响应时间 | Excessive Temperature Difference Level 1 Recovery Response Time | 0x19CC
B+B-/P+/P-温度过高一级告警值 | B+/B-/P+/P- Temperature High Level 1 Alarm Value | 0x190D | ℃ |  |  | B+/B-/P+/P-温度过高一级告警响应时间 | B+/B-/P+/P- Temperature High Level 1 Alarm Response Time | 0x194D |  | B+/B-/P+/P-温度过高一级恢复值 | B+/B-/P+/P- Temperature High Level 1 Recovery Value | 0x198D | ℃ |  | B+/B-/P+/P-温度过高一级恢复响应时间 | B+/B-/P+/P- Temperature High Level 1 Recovery Response Time | 0x19CD
环境高温一级告警值 | Ambient High Temperature Level 1 Alarm Value | 0x190E |  |  |  | 环境高温一级告警响应时间 | Ambient High Temperature Level 1 Alarm Response Time | 0x194E |  | 环境高温一级恢复值 | Ambient High Temperature Level 1 Recovery Value | 0x198E |  |  | 环境高温一级恢复响应时间 | Ambient High Temperature Level 1 Recovery Response Time | 0x19CE
预留 | Reserved | 0x190F~0x1915 |  |  |  | 预留 | Reserved | 0x194E~0x1955 |  | 预留 | Reserved | 0x198E~0x1995 |  |  | 预留 | Reserved | 0x19CE~0x19D5
单体过压二级故障值 | Cell Overvoltage Level 2 Fault Value | 0x1916 | mV |  |  | 单体过压二级故障响应时间 | Cell Overvoltage Level 2 Fault Response Time | 0x1956 |  | 单体过压二级恢复值 | Cell Overvoltage Level 2 Recovery Value | 0x1996 | mV |  | 单体过压二级恢复响应时间 | Cell Overvoltage Level 2 Recovery Response Time | 0x19D6
单体欠压二级故障值 | Cell Undervoltage Level 2 Fault Value | 0x1917 | mV |  |  | 单体欠压二级故障响应时间 | Cell Undervoltage Level 2 Fault Response Time | 0x1957 |  | 单体欠压二级恢复值 | Cell Undervoltage Level 2 Recovery Value | 0x1997 | mV |  | 单体欠压二级恢复响应时间 | Cell Undervoltage Level 2 Recovery Response Time | 0x19D7
总压过压二级告警值 | Total Voltage Overvoltage Level 2 Alarm Value | 0x1918 | 0.1V |  |  | 总压过压二级告警响应时间 | Total Voltage Overvoltage Level 2 Alarm Response Time | 0x1958 |  | 总压过压二级恢复值 | Total Voltage Overvoltage Level 2 Recovery Value | 0x1998 | 0.1V |  | 总压过压二级恢复响应时间 | Total Voltage Overvoltage Level 2 Recovery Response Time | 0x19D8
总压欠压二级告警值 | Total Voltage Undervoltage Level 2 Alarm Value | 0x1919 | 0.1V |  |  | 总压欠压二级告警响应时间 | Total Voltage Undervoltage Level 2 Alarm Response Time | 0x1959 |  | 总压欠压二级恢复值 | Total Voltage Undervoltage Level 2 Recovery Value | 0x1999 | 0.1V |  | 总压欠压二级恢复响应时间 | Total Voltage Undervoltage Level 2 Recovery Response Time | 0x19D9
单体压差二级告警值 | Cell Voltage Difference Level 2 Alarm Value | 0x191A | mV |  |  | 单体压差二级告警响应时间 | Cell Voltage Difference Level 2 Alarm Response Time | 0x195A |  | 单体压差二级恢复值 | Cell Voltage Difference Level 2 Recovery Value | 0x199A | mV |  | 单体压差二级恢复响应时间 | Cell Voltage Difference Level 2 Recovery Response Time | 0x19DA
高压箱放电过流二级故障值 | High-Voltage Box Discharge Overcurrent Level 2 Fault Value | 0x191B | A |  |  | 高压箱放电过流二级故障响应时间 | High-Voltage Box Discharge Overcurrent Level 2 Fault Response Time | 0x195B |  | 高压箱放电过流二级恢复值 | High-Voltage Box Discharge Overcurrent Level 2 Recovery Value | 0x199B | A |  | 高压箱放电过流二级恢复响应时间 | High-Voltage Box Discharge Overcurrent Level 2 Recovery Response Time | 0x19DB
充电过流二级故障值 | Charge Overcurrent Level 2 Fault Value | 0x191C | A |  |  | 充电过流二级故障响应时间 | Charge Overcurrent Level 2 Fault Response Time | 0x195C |  | 充电过流二级恢复值 | Charge Overcurrent Level 2 Recovery Value | 0x199C | A |  | 充电过流二级恢复响应时间 | Charge Overcurrent Level 2 Recovery Response Time | 0x19DC
绝缘电阻二级告警值 | Insulation Resistance Level 2 Alarm Value | 0x191D | Ω/V |  |  | 绝缘电阻二级告警响应时间 | Insulation Resistance Level 2 Alarm Response Time | 0x195D |  | 绝缘电阻二级恢复值 | Insulation Resistance Level 2 Recovery Value | 0x199D | Ω/V |  | 绝缘电阻二级恢复响应时间 | Insulation Resistance Level 2 Recovery Response Time | 0x19DD
充电高温二级故障值 | Charging High Temperature Level 2 Fault Value | 0x191E | ℃ |  |  | 充电高温二级故障响应时间 | Charging High Temperature Level 2 Fault Response Time | 0x195E |  | 充电高温二级恢复值 | Charging High Temperature Level 2 Recovery Value | 0x199E | ℃ |  | 充电高温二级恢复响应时间 | Charging High Temperature Level 2 Recovery Response Time | 0x19DE
放电高温二级故障值 | Discharging High Temperature Level 2 Fault Value | 0x191F | ℃ |  |  | 放电高温二级故障响应时间 | Discharging High Temperature Level 2 Fault Response Time | 0x195F |  | 放电高温二级恢复值 | Discharging High Temperature Level 2 Recovery Value | 0x199F | ℃ |  | 放电高温二级恢复响应时间 | Discharging High Temperature Level 2 Recovery Response Time | 0x19DF
充电低温二级故障值 | Charging Low Temperature Level 2 Fault Value | 0x1920 | ℃ |  |  | 充电低温二级故障响应时间 | Charging Low Temperature Level 2 Fault Response Time | 0x1960 |  | 充电低温二级恢复值 | Charging Low Temperature Level 2 Recovery Value | 0x19A0 | ℃ |  | 充电低温二级恢复响应时间 | Charging Low Temperature Level 2 Recovery Response Time | 0x19E0
放电低温二级故障值 | Discharging Low Temperature Level 2 Fault Value | 0x1921 | ℃ |  |  | 放电低温二级故障响应时间 | Discharging Low Temperature Level 2 Fault Response Time | 0x1961 |  | 放电低温二级恢复值 | Discharging Low Temperature Level 2 Recovery Value | 0x19A1 | ℃ |  | 放电低温二级恢复响应时间 | Discharging Low Temperature Level 2 Recovery Response Time | 0x19E1
温差过大二级告警值 | Excessive Temperature Difference Level 2 Alarm Value | 0x1922 | ℃ |  |  | 温差过大二级告警响应时间 | Excessive Temperature Difference Level 2 Alarm Response Time | 0x1962 |  | 温差过大二级恢复值 | Excessive Temperature Difference Level 2 Recovery Value | 0x19A2 | ℃ |  | 温差过大二级恢复响应时间 | Excessive Temperature Difference Level 2 Recovery Response Time | 0x19E2
B+/B-/P+/P-温度过高二级告警值 | B+/B-/P+/P- Temperature High Level 2 Alarm Value | 0x1923 | ℃ |  |  | B+/B-/P+/P-温度过高二级告警响应时间 | B+/B-/P+/P- Temperature High Level 2 Alarm Response Time | 0x1963 |  | B+/B-/P+/P-温度过高二级恢复值 | B+/B-/P+/P- Temperature High Level 2 Recovery Value | 0x19A3 | ℃ |  | B+/B-/P+/P-温度过高二级恢复响应时间 | B+/B-/P+/P- Temperature High Level 2 Recovery Response Time | 0x19E3
环境高温二级告警值 | Ambient High Temperature Level 2 Alarm Value | 0x1924 |  |  |  | 环境高温二级告警响应时间 | Ambient High Temperature Level 2 Alarm Response Time | 0x1964 |  | 环境高温二级恢复值 | Ambient High Temperature Level 2 Recovery Value | 0x19A4 |  |  | 环境高温二级恢复值 | Ambient High Temperature Level 2 Recovery Value | 0x19E4
预留 | Reserved | 0x1924~0x192A |  |  |  | 预留 | Reserved | 0x1964~0x196A |  | 预留 | Reserved | 0x19A4~0x19AA |  |  | 预留 | Reserved | 0x19E4~0x19EA
单体过压三级严重故障值 | Cell Overvoltage Level 3 Severe Fault Value | 0x192B | mV |  |  | 单体过压三级严重故障响应时间 | Cell Overvoltage Level 3 Severe Fault Response Time | 0x196B |  | 单体过压三级恢复值 | Cell Overvoltage Level 3 Recovery Value | 0x19AB | mV |  | 单体过压三级恢复响应时间 | Cell Overvoltage Level 3 Recovery Response Time | 0x19EB
单体欠压三级严重故障值 | Cell Undervoltage Level 3 Severe Fault Value | 0x192C | mV |  |  | 单体欠压三级严重故障响应时间 | Cell Undervoltage Level 3 Severe Fault Response Time | 0x196C |  | 单体欠压三级恢复值 | Cell Undervoltage Level 3 Recovery Value | 0x19AC | mV |  | 单体欠压三级恢复响应时间 | Cell Undervoltage Level 3 Recovery Response Time | 0x19EC
总压过压三级保护值 | Total Voltage Overvoltage Level 3 Protection Value | 0x192D | 0.1V |  |  | 总压过压三级保护响应时间 | Total Voltage Overvoltage Level 3 Protection Response Time | 0x196D |  | 总压过压三级恢复值 | Total Voltage Overvoltage Level 3 Recovery Value | 0x19AD | 0.1V |  | 总压过压三级恢复响应时间 | Total Voltage Overvoltage Level 3 Recovery Response Time | 0x19ED
总压欠压三级保护值 | Total Voltage Undervoltage Level 3 Protection Value | 0x192E | 0.1V |  |  | 总压欠压三级保护响应时间 | Total Voltage Undervoltage Level 3 Protection Response Time | 0x196E |  | 总压欠压三级恢复值 | Total Voltage Undervoltage Level 3 Recovery Value | 0x19AE | 0.1V |  | 总压欠压三级恢复响应时间 | Total Voltage Undervoltage Level 3 Recovery Response Time | 0x19EE
单体压差三级告警值 | Cell Voltage Difference Level 3 Alarm Value | 0x192F | mV |  |  | 单体压差三级告警响应时间 | Cell Voltage Difference Level 3 Alarm Response Time | 0x196F |  | 单体压差三级恢复值 | Cell Voltage Difference Level 3 Recovery Value | 0x19AF | mV |  | 单体压差三级恢复响应时间 | Cell Voltage Difference Level 3 Recovery Response Time | 0x19EF
高压箱放电过流三级严重故障值 | High-Voltage Box Discharge Overcurrent Level 3 Severe Fault Value | 0x1930 | A |  |  | 高压箱放电过流三级严重故障响应时间 | High-Voltage Box Discharge Overcurrent Level 3 Severe Fault Response Time | 0x1970 |  | 高压箱放电过流三级恢复值 | High-Voltage Box Discharge Overcurrent Level 3 Recovery Value | 0x19B0 | A |  | 高压箱放电过流三级恢复响应时间 | High-Voltage Box Discharge Overcurrent Level 3 Recovery Response Time | 0x19F0
充电过流三级严重故障值 | Charge Overcurrent Level 3 Severe Fault Value | 0x1931 | A |  |  | 充电过流三级严重故障响应时间 | Charge Overcurrent Level 3 Severe Fault Response Time | 0x1971 |  | 充电过流三级恢复值 | Charge Overcurrent Level 3 Recovery Value | 0x19B1 | A |  | 充电过流三级恢复响应时间 | Charge Overcurrent Level 3 Recovery Response Time | 0x19F1
绝缘电阻三级告警值 | Insulation Resistance Level 3 Alarm Value | 0x1932 | Ω/V |  | Reserved, Not Currently Used | 绝缘电阻三级告警响应时间 | Insulation Resistance Level 3 Alarm Response Time | 0x1972 | 预留，暂不使用 | 绝缘电阻三级恢复值 | Insulation Resistance Level 3 Recovery Value | 0x19B2 | Ω/V | Reserved, Not Currently Used | 绝缘电阻三级恢复响应时间 | Insulation Resistance Level 3 Recovery Response Time | 0x19F2 | Reserved, Not Currently Used
充电高温三级严重故障值 | Charging High Temperature Level 3 Severe Fault Value | 0x1933 | ℃ |  |  | 充电高温三级严重故障响应时间 | Charging High Temperature Level 3 Severe Fault Response Time | 0x1973 |  | 充电高温三级恢复值 | Charging High Temperature Level 3 Recovery Value | 0x19B3 | ℃ |  | 充电高温三级恢复响应时间 | Charging High Temperature Level 3 Recovery Response Time | 0x19F3
放电高温三级严重故障值 | Discharging High Temperature Level 3 Severe Fault Value | 0x1934 | ℃ |  |  | 放电高温三级严重故障响应时间 | Discharging High Temperature Level 3 Severe Fault Response Time | 0x1974 |  | 放电高温三级恢复值 | Discharging High Temperature Level 3 Recovery Value | 0x19B4 | ℃ |  | 放电高温三级恢复响应时间 | Discharging High Temperature Level 3 Recovery Response Time | 0x19F4
充电低温三级严重故障值 | Charging Low Temperature Level 3 Severe Fault Value | 0x1935 | ℃ |  | Reserved, Not Currently Used | 充电低温三级严重故障响应时间 | Charging Low Temperature Level 3 Severe Fault Response Time | 0x1975 | 预留，暂不使用 | 充电低温三级恢复值 | Charging Low Temperature Level 3 Recovery Value | 0x19B5 | ℃ | Reserved, Not Currently Used | 充电低温三级恢复响应时间 | Charging Low Temperature Level 3 Recovery Response Time | 0x19F5 | Reserved, Not Currently Used
放电低温三级严重故障值 | Discharging Low Temperature Level 3 Severe Fault Value | 0x1936 | ℃ |  | Reserved, Not Currently Used | 放电低温三级严重故障响应时间 | Discharging Low Temperature Level 3 Severe Fault Response Time | 0x1976 | 预留，暂不使用 | 放电低温三级恢复值 | Discharging Low Temperature Level 3 Recovery Value | 0x19B6 | ℃ | Reserved, Not Currently Used | 放电低温三级恢复响应时间 | Discharging Low Temperature Level 3 Recovery Response Time | 0x19F6 | Reserved, Not Currently Used
温差过大三级告警值 | Excessive Temperature Difference Level 3 Alarm Value | 0x1937 | ℃ |  |  | 温差过大三级告警响应时间 | Excessive Temperature Difference Level 3 Alarm Response Time | 0x1977 |  | 温差过大三级恢复值 | Excessive Temperature Difference Level 3 Recovery Value | 0x19B7 | ℃ |  | 温差过大三级恢复响应时间 | Excessive Temperature Difference Level 3 Recovery Response Time | 0x19F7
B+/B-/P+/P-温度过高三级告警值 | B+/B-/P+/P- Temperature High Level 3 Alarm Value | 0x1938 | ℃ |  |  | B+/B-/P+/P-温度过高三级告警响应时间 | B+/B-/P+/P- Temperature High Level 3 Alarm Response Time | 0x1978 |  | B+/B-/P+/P-温度过高三级恢复值 | B+/B-/P+/P- Temperature High Level 3 Recovery Value | 0x19B8 | ℃ |  | B+/B-/P+/P-温度过高三级恢复响应时间 | B+/B-/P+/P- Temperature High Level 3 Recovery Response Time | 0x19F8
环境高温三级告警值 | Ambient High Temperature Level 3 Alarm Value | 0x1939 |  |  |  | 环境高温三级告警响应时间 | Ambient High Temperature Level 3 Alarm Response Time | 0x1979 |  | 环境高温三级恢复值 | Ambient High Temperature Level 3 Recovery Value | 0x19B9 |  |  | 环境高温三级恢复响应时间 | Ambient High Temperature Level 3 Recovery Response Time | 0x19F9
预留 | Reserved | 0x1939~0x193F |  |  |  | 预留 | Reserved | 0x1979~0x197F |  | 预留 | Reserved | 0x19B9~0x19BF |  |  | 预留 | Reserved | 0x19F9~0x19FF
单体过压四级严重故障值 | Cell Overvoltage Level 4 Severe Fault Value | 0x1A00 | mV |  |  | 单体过压四级严重故障响应时间 | Cell Overvoltage Level 4 Severe Fault Response Time | 0x1A16 |  | 单体过压四级恢复值 | Cell Overvoltage Level 4 Recovery Value | 0x1A2B | mV |  | 单体过压四级恢复响应时间 | Cell Overvoltage Level 4 Recovery Response Time | 0x1A40
单体欠压四级严重故障值 | Cell Undervoltage Level 4 Severe Fault Value | 0x1A01 | mV |  |  | 单体欠压四级严重故障响应时间 | Cell Undervoltage Level 4 Severe Fault Response Time | 0x1A17 |  | 单体欠压四级恢复值 | Cell Undervoltage Level 4 Recovery Value | 0x1A2C | mV |  | 单体欠压四级恢复响应时间 | Cell Undervoltage Level 4 Recovery Response Time | 0x1A41
总压过压四级保护值 | Total Voltage Overvoltage Level 4 Protection Value | 0x1A02 | 0.1V |  |  | 总压过压四级保护响应时间 | Total Voltage Overvoltage Level 4 Protection Response Time | 0x1A18 |  | 总压过压四级恢复值 | Total Voltage Overvoltage Level 4 Recovery Value | 0x1A2D | 0.1V |  | 总压过压四级恢复响应时间 | Total Voltage Overvoltage Level 4 Recovery Response Time | 0x1A42
总压欠压四级保护值 | Total Voltage Undervoltage Level 4 Protection Value | 0x1A03 | 0.1V |  |  | 总压欠压四级保护响应时间 | Total Voltage Undervoltage Level 4 Protection Response Time | 0x1A19 |  | 总压欠压四级恢复值 | Total Voltage Undervoltage Level 4 Recovery Value | 0x1A2E | 0.1V |  | 总压欠压四级恢复响应时间 | Total Voltage Undervoltage Level 4 Recovery Response Time | 0x1A43
单体压差四级告警值 | Cell Voltage Difference Level 4 Alarm Value | 0x1A04 | mV |  |  | 单体压差四级告警响应时间 | Cell Voltage Difference Level 4 Alarm Response Time | 0x1A1A |  | 单体压差四级恢复值 | Cell Voltage Difference Level 4 Recovery Value | 0x1A2F | mV |  | 单体压差四级恢复响应时间 | Cell Voltage Difference Level 4 Recovery Response Time | 0x1A44
高压箱放电过流四级严重故障值 | High-Voltage Box Discharge Overcurrent Level 4 Severe Fault Value | 0x1A05 | A |  |  | 高压箱放电过流四级严重故障响应时间 | High-Voltage Box Discharge Overcurrent Level 4 Severe Fault Response Time | 0x1A1B |  | 高压箱放电过流四级恢复值 | High-Voltage Box Discharge Overcurrent Level 4 Recovery Value | 0x1A30 | A |  | 高压箱放电过流四级恢复响应时间 | High-Voltage Box Discharge Overcurrent Level 4 Recovery Response Time | 0x1A45
充电过流四级严重故障值 | Charge Overcurrent Level 4 Severe Fault Value | 0x1A06 | A |  |  | 充电过流四级严重故障响应时间 | Charge Overcurrent Level 4 Severe Fault Time | 0x1A1C |  | 充电过流四级恢复值 | Charge Overcurrent Level 4 Recovery Value | 0x1A31 | A |  | 充电过流四级恢复响应时间 | Charge Overcurrent Level 4 Recovery Response Time | 0x1A46
绝缘电阻四级告警值 | Insulation Resistance Level 4 Alarm Value | 0x1A07 | Ω/V |  | Reserved, Not Currently Used | 绝缘电阻四级告警响应时间 | Insulation Resistance Level 4 Alarm Response Time | 0x1A1D | 预留，暂不使用 | 绝缘电阻四级恢复值 | Insulation Resistance Level 4 Recovery Value | 0x1A32 | Ω/V | Reserved, Not Currently Used | 绝缘电阻四级恢复响应时间 | Insulation Resistance Level 4 Recovery Response Time | 0x1A47
充电高温四级严重故障值 | Charging High Temperature Level 4 Severe Fault Value | 0x1A08 | ℃ |  |  | 充电高温四级严重故障响应时间 | Charging High Temperature Level 4 Severe Fault Response Time | 0x1A1E |  | 充电高温四级恢复值 | Charging High Temperature Level 4 Recovery Value | 0x1A33 | ℃ |  | 充电高温四级恢复响应时间 | Charging High Temperature Level 4 Recovery Response Time | 0x1A48
放电高温四级严重故障值 | Discharging High Temperature Level 4 Severe Fault Value | 0x1A09 | ℃ |  |  | 放电高温四级严重故障响应时间 | Discharging High Temperature Level 4 Severe Fault Response Time | 0x1A1F |  | 放电高温四级恢复值 | Discharging High Temperature Level 4 Recovery Value | 0x1A34 | ℃ |  | 放电高温四级恢复响应时间 | Discharging High Temperature Level 4 Recovery Response Time | 0x1A49
充电低温四级严重故障值 | Charging Low Temperature Level 4 Severe Fault Value | 0x1A0A | ℃ |  | Reserved, Not Currently Used | 充电低温四级严重故障响应时间 | Charging Low Temperature Level 4 Severe Fault Response Time | 0x1A20 | 预留，暂不使用 | 充电低温四级恢复值 | Charging Low Temperature Level 4 Recovery Value | 0x1A35 | ℃ | Reserved, Not Currently Used | 充电低温四级恢复响应时间 | Charging Low Temperature Level 4 Recovery Response Time | 0x1A4A
放电低温四级严重故障值 | Discharging Low Temperature Level 4 Severe Fault Value | 0x1A0B | ℃ |  | Reserved, Not Currently Used | 放电低温四级严重故障响应时间 | Discharging Low Temperature Level 4 Severe Fault Response Time | 0x1A21 | 预留，暂不使用 | 放电低温四级恢复值 | Discharging Low Temperature Level 4 Recovery Value | 0x1A36 | ℃ | Reserved, Not Currently Used | 放电低温四级恢复响应时间 | Discharging Low Temperature Level 4 Recovery Response Time | 0x1A4B
温差过大四级告警值 | Excessive Temperature Difference Level 4 Alarm Value | 0x1A0C | ℃ |  |  | 温差过大四级告警响应时间 | Excessive Temperature Difference Level 4 Alarm Response Time | 0x1A22 |  | 温差过大四级恢复值 | Excessive Temperature Difference Level 4 Recovery Value | 0x1A37 | ℃ |  | 温差过大四级恢复响应时间 | Excessive Temperature Difference Level 4 Recovery Response Time | 0x1A4C
B+/B-/P+/P-温度过高四级告警值 | B+/B-/P+/P- Temperature High Level 4 Alarm Value | 0x1A0D | ℃ |  |  | B+/B-/P+/P-温度过高四级告警响应时间 | B+/B-/P+/P- Temperature High Level 4 Alarm Response Time | 0x1A23 |  | B+/B-/P+/P-温度过高四级恢复值 | B+/B-/P+/P- Temperature High Level 4 Recovery Value | 0x1A38 | ℃ |  | B+/B-/P+/P-温度过高四级恢复响应时间 | B+/B-/P+/P- Temperature High Level 4 Recovery Response Time | 0x1A4D
环境高温四级告警值 | Ambient High Temperature Level 4 Alarm Value | 0x1A0E |  |  |  | 环境高温四级告警响应时间 | Ambient High Temperature Level 4 Alarm Response Time | 0x1A24 |  | 环境高温四级恢复值 | Ambient High Temperature Level 4 Recovery Value | 0x1A39 |  |  | 环境高温四级恢复响应时间 | Ambient High Temperature Level 4 Recovery Response Time | 0x1A4E
预留 | Reserved | 0x1A0F~0x1A15 |  |  |  | 预留 | Reserved | 0x1A24~0x1A2A |  | 预留 | Reserved | 0x1A39~0x1A3F |  |  | 预留 | Reserved | 0x1A4E~0x1A55

## Discrete quantities (fault code
The fault code is the discrete input address
|  | 00~FF |  |  |  |  | 100~1FF |  |  |  |  | 200~2FF
Cluster fault code | Level 1 Fault( 0x1000~0x10FF) |  |  |  |  | Level 2 Fault( 0x1100~0x11FF) |  |  |  |  | Level 3 Fault( 0x1200~0x12FF)
| Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level | Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level | Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level
| bit 0 | 充电单体高压 | Charge Cell Overvoltage | 0x00 | 1 | bit 0 | 充电单体高压 | Charge Cell Overvoltage | 0x00 | 2 | bit 0 | 充电单体高压 | Charge Cell Overvoltage | 0x00 | 3
| bit 1 | 放电单体高压 | Discharge Cell Overvoltage | 0x01 | 1 | bit 1 | 放电单体高压 | Discharge Cell Overvoltage | 0x01 | 2 | bit 1 | 放电单体高压 | Discharge Cell Overvoltage | 0x01 | 3
| bit 2 | 充电单体低压 | Charge Cell Undervoltage | 0x02 | 1 | bit 2 | 充电单体低压 | Charge Cell Undervoltage | 0x02 | 2 | bit 2 | 充电单体低压 | Charge Cell Undervoltage | 0x02 | 3
| bit 3 | 放电单体低压 | Discharge Cell Undervoltage | 0x03 | 1 | bit 3 | 放电单体低压 | Discharge Cell Undervoltage | 0x03 | 2 | bit 3 | 放电单体低压 | Discharge Cell Undervoltage | 0x03 | 3
| bit 4 | 充电总压高 | Charge Total Voltage High | 0x04 | 1 | bit 4 | 充电总压高 | Charge Total Voltage High | 0x04 | 2 | bit 4 | 充电总压高 | Charge Total Voltage High | 0x04 | 3
| bit 5 | 放电总压高 | Discharge Total Voltage High | 0x05 | 1 | bit 5 | 放电总压高 | Discharge Total Voltage High | 0x05 | 2 | bit 5 | 放电总压高 | Discharge Total Voltage High | 0x05 | 3
| bit 6 | 充电总压低 | Charge Total Voltage Low | 0x06 | 1 | bit 6 | 充电总压低 | Charge Total Voltage Low | 0x06 | 2 | bit 6 | 充电总压低 | Charge Total Voltage Low | 0x06 | 3
| bit 7 | 放电总压低 | Discharge Total Voltage Low | 0x07 | 1 | bit 7 | 放电总压低 | Discharge Total Voltage Low | 0x07 | 2 | bit 7 | 放电总压低 | Discharge Total Voltage Low | 0x07 | 3
| bit 8 | 充电总压差 | Charge Total Voltage Difference | 0x08 | 1 | bit 8 | 充电总压差 | Charge Total Voltage Difference | 0x08 | 2 | bit 8 | 充电总压差 | Charge Total Voltage Difference | 0x08 | 3
| bit 9 | 放电总压差 | Discharge Total Voltage Difference | 0x09 | 1 | bit 9 | 放电总压差 | Discharge Total Voltage Difference | 0x09 | 2 | bit 9 | 放电总压差 | Discharge Total Voltage Difference | 0x09 | 3
| bit 10 | 充电压差 | Charge Voltage Difference | 0x0A | 1 | bit 10 | 充电压差 | Charge Voltage Difference | 0x0A | 2 | bit 10 | 充电压差 | Charge Voltage Difference | 0x0A | 3
| bit 11 | 放电压差 | Discharge Voltage Difference | 0x0B | 1 | bit 11 | 放电压差 | Discharge Voltage Difference | 0x0B | 2 | bit 11 | 放电压差 | Discharge Voltage Difference | 0x0B | 3
| bit 12 | 充电高温 | Charging High Temperature | 0x0C | 1 | bit 12 | 充电高温 | Charging High Temperature | 0x0C | 2 | bit 12 | 充电高温 | Charging High Temperature | 0x0C | 3
| bit 13 | 放电高温 | Discharging High Temperature | 0x0D | 1 | bit 13 | 放电高温 | Discharging High Temperature | 0x0D | 2 | bit 13 | 放电高温 | Discharging High Temperature | 0x0D | 3
| bit 14 | 充电低温 | Charging Low Temperature | 0x0E | 1 | bit 14 | 充电低温 | Charging Low Temperature | 0x0E | 2 | bit 14 | 充电低温 | Charging Low Temperature | 0x0E | 3
| bit 15 | 放电低温 | Discharging Low Temperature | 0x0F | 1 | bit 15 | 放电低温 | Discharging Low Temperature | 0x0F | 2 | bit 15 | 放电低温 | Discharging Low Temperature | 0x0F | 3
| bit 16 | 充电温差 | Charging Temperature Difference | 0x10 | 1 | bit 16 | 充电温差 | Charging Temperature Difference | 0x10 | 2 | bit 16 | 充电温差 | Charging Temperature Difference | 0x10 | 3
| bit 17 | 放电温差 | Discharging Temperature Difference | 0x11 | 1 | bit 17 | 放电温差 | Discharging Temperature Difference | 0x11 | 2 | bit 17 | 放电温差 | Discharging Temperature Difference | 0x11 | 3
| bit 18 | 充电过流 | Charging Overcurrent | 0x12 | 1 | bit 18 | 充电过流 | Charging Overcurrent | 0x12 | 2 | bit 18 | 充电过流 | Charging Overcurrent | 0x12 | 3
| bit 19 | 持续放电过流 | Continuous Discharging Overcurrent | 0x13 | 1 | bit 19 | 持续放电过流 | Continuous Discharging Overcurrent | 0x13 | 2 | bit 19 | 持续放电过流 | Continuous Discharging Overcurrent | 0x13 | 3
| bit 20 | 瞬时放电过流 | Instantaneous Discharging Overcurrent | 0x14 | 1 | bit 20 | 瞬时放电过流 | Instantaneous Discharging Overcurrent | 0x14 | 2 | bit 20 | 瞬时放电过流 | Instantaneous Discharging Overcurrent | 0x14 | 3
| bit 21 | SOC高 | SOC High | 0x15 | 1 | bit 21 | SOC高 | SOC High | 0x15 | 2 | bit 21 | SOC高 | SOC High | 0x15 | 3
| bit 22 | SOC低 | SOC Low | 0x16 | 1 | bit 22 | SOC低 | SOC Low | 0x16 | 2 | bit 22 | SOC低 | SOC Low | 0x16 | 3
| bit 23 | 漏电 | Leakage | 0x17 | 1 | bit 23 | 漏电 | Leakage | 0x17 | 2 | bit 23 | 漏电 | Leakage | 0x17 | 3
| bit 24 | 充电加热过温 | Charging Heater Overtemperature | 0x18 | 1 | bit 24 | 充电加热过温 | Charging Heater Overtemperature | 0x18 | 2 | bit 24 | 充电加热过温 | Charging Heater Overtemperature | 0x18 | 3
| bit 25 | 放电加热过温 | Discharging Heater Overtemperature | 0x19 | 1 | bit 25 | 放电加热过温 | Discharging Heater Overtemperature | 0x19 | 2 | bit 25 | 放电加热过温 | Discharging Heater Overtemperature | 0x19 | 3
| bit 26 | 充电加热温差过大 | Charging Heater Excessive Temperature Difference | 0x1A | 1 | bit 26 | 充电加热温差过大 | Charging Heater Excessive Temperature Difference | 0x1A | 2 | bit 26 | 充电加热温差过大 | Charging Heater Excessive Temperature Difference | 0x1A | 3
| bit 27 | 放电加热温差过大 | Discharging Heater Excessive Temperature Difference | 0x1B | 1 | bit 27 | 放电加热温差过大 | Discharging Heater Excessive Temperature Difference | 0x1B | 2 | bit 27 | 放电加热温差过大 | Discharging Heater Excessive Temperature Difference | 0x1B | 3
| bit 28 | 充电加热超时 | Charging Heater Timeout | 0x1C | 1 | bit 28 | 充电加热超时 | Charging Heater Timeout | 0x1C | 2 | bit 28 | 充电加热超时 | Charging Heater Timeout | 0x1C | 3
| bit 29 | 放电加热超时 | Discharging Heater Timeout | 0x1D | 1 | bit 29 | 放电加热超时 | Discharging Heater Timeout | 0x1D | 2 | bit 29 | 放电加热超时 | Discharging Heater Timeout | 0x1D | 3
| bit 30 | 充电加热过流 | Charging Heater Overcurrent | 0x1E | 1 | bit 30 | 充电加热过流 | Charging Heater Overcurrent | 0x1E | 2 | bit 30 | 充电加热过流 | Charging Heater Overcurrent | 0x1E | 3
| bit 31 | 放电加热过流 | Discharging Heater Overcurrent | 0x1F | 1 | bit 31 | 放电加热过流 | Discharging Heater Overcurrent | 0x1F | 2 | bit 31 | 放电加热过流 | Discharging Heater Overcurrent | 0x1F | 3
| bit 32 | SOC跳变 | SOC Jump | 0x20 | 1 | bit 32 | SOC跳变 | SOC Jump | 0x20 | 2 | bit 32 | SOC跳变 | SOC Jump | 0x20 | 3
| bit 33 | 供电电压过低 | Supply Voltage Too Low | 0x21 | 1 | bit 33 | 供电电压过低 | Supply Voltage Too Low | 0x21 | 2 | bit 33 | 供电电压过低 | Supply Voltage Too Low | 0x21 | 3
| bit 34 | 充电极柱过温 | Charging Terminal Post Overtemperature | 0x22 | 1 | bit 34 | 充电极柱过温 | Charging Terminal Post Overtemperature | 0x22 | 2 | bit 34 | 充电极柱过温 | Charging Terminal Post Overtemperature | 0x22 | 3
| bit 35 | 放电极柱过温 | Discharging Terminal Post Overtemperature | 0x23 | 1 | bit 35 | 放电极柱过温 | Discharging Terminal Post Overtemperature | 0x23 | 2 | bit 35 | 放电极柱过温 | Discharging Terminal Post Overtemperature | 0x23 | 3
| bit 36 | 充电极柱温差过大 | Charging Terminal Post Excessive Temperature Difference | 0x24 | 1 | bit 36 | 充电极柱温差过大 | Charging Terminal Post Excessive Temperature Difference | 0x24 | 2 | bit 36 | 充电极柱温差过大 | Charging Terminal Post Excessive Temperature Difference | 0x24 | 3
| bit 37 | 放电极柱温差过大 | Discharging Terminal Post Excessive Temperature Difference | 0x25 | 1 | bit 37 | 放电极柱温差过大 | Discharging Terminal Post Excessive Temperature Difference | 0x25 | 2 | bit 37 | 放电极柱温差过大 | Discharging Terminal Post Excessive Temperature Difference | 0x25 | 3
| bit 38 | 充电电流异常 | Charging Current Anomaly | 0x26 | 1 | bit 38 | 充电电流异常 | Charging Current Anomaly | 0x26 | 2 | bit 38 | 充电电流异常 | Charging Current Anomaly | 0x26 | 3
| bit 39 | 供电电压过高 | Supply Voltage Too High | 0x27 | 1 | bit 39 | 供电电压过高 | Supply Voltage Too High | 0x27 | 2 | bit 39 | 供电电压过高 | Supply Voltage Too High | 0x27 | 3
| bit 40 | 电压排线 | Voltage Wiring | 0x28 | 1 | bit 40 | 电压排线 | Voltage Wiring | 0x28 | 2 | bit 40 | 电压排线 | Voltage Wiring | 0x28 | 3
| bit 41 | 温感排线 | Temperature Sensor Wiring | 0x29 | 1 | bit 41 | 温感排线 | Temperature Sensor Wiring | 0x29 | 2 | bit 41 | 温感排线 | Temperature Sensor Wiring | 0x29 | 3
| bit 42 | 内网通信 | Internal Network Communication | 0x2A | 1 | bit 42 | 内网通信 | Internal Network Communication | 0x2A | 2 | bit 42 | 内网通信 | Internal Network Communication | 0x2A | 3
| bit 43 | 插座正温度过高 | Receptacle Positive Temperature Too High | 0x2B | 1 | bit 43 | 插座正温度过高 | Receptacle Positive Temperature Too High | 0x2B | 2 | bit 43 | 插座正温度过高 | Receptacle Positive Temperature Too High | 0x2B | 3
| bit 44 | 插座负温度过高 | Receptacle Negative Temperature Too High | 0x2C | 1 | bit 44 | 插座负温度过高 | Receptacle Negative Temperature Too High | 0x2C | 2 | bit 44 | 插座负温度过高 | Receptacle Negative Temperature Too High | 0x2C | 3
| bit 45 | 预充失败 | Pre-charge Failure | 0x2D | 1 | bit 45 | 预充失败 | Pre-charge Failure | 0x2D | 2 | bit 45 | 预充失败 | Pre-charge Failure | 0x2D | 3
| bit 46 | 电流异常 | Current Anomaly | 0x2E | 1 | bit 46 | 电流异常 | Current Anomaly | 0x2E | 2 | bit 46 | 电流异常 | Current Anomaly | 0x2E | 3
| bit 47 | BMS初始化故障 | BMS Initialization Fault | 0x2F | 1 | bit 47 | BMS初始化故障 | BMS Initialization Fault | 0x2F | 2 | bit 47 | BMS初始化故障 | BMS Initialization Fault | 0x2F | 3
| bit 48 | HVIL故障 | HVIL Fault | 0x30 | 1 | bit 48 | HVIL故障 | HVIL Fault | 0x30 | 2 | bit 48 | HVIL故障 | HVIL Fault | 0x30 | 3
| bit 49 | 继电器故障 | Relay Fault | 0x31 | 1 | bit 49 | 继电器故障 | Relay Fault | 0x31 | 2 | bit 49 | 继电器故障 | Relay Fault | 0x31 | 3
| bit 50 | 加热故障 | Heating Fault | 0x32 | 1 | bit 50 | 加热故障 | Heating Fault | 0x32 | 2 | bit 50 | 加热故障 | Heating Fault | 0x32 | 3
| bit 51 | 加热温感异常 | Heater Temperature Sensor Anomaly | 0x33 | 1 | bit 51 | 加热温感异常 | Heater Temperature Sensor Anomaly | 0x33 | 2 | bit 51 | 加热温感异常 | Heater Temperature Sensor Anomaly | 0x33 | 3
| bit 52 | 极柱温感异常 | Terminal Post Temperature Sensor Anomaly | 0x34 | 1 | bit 52 | 极柱温感异常 | Terminal Post Temperature Sensor Anomaly | 0x34 | 2 | bit 52 | 极柱温感异常 | Terminal Post Temperature Sensor Anomaly | 0x34 | 3
| bit 53 | 电池数不匹配 | Mismatched Battery Count | 0x35 | 1 | bit 53 | 电池数不匹配 | Mismatched Battery Count | 0x35 | 2 | bit 53 | 电池数不匹配 | Mismatched Battery Count | 0x35 | 3
| bit 54 | 温感数不匹配 | Mismatched Temperature Sensor Count | 0x36 | 1 | bit 54 | 温感数不匹配 | Mismatched Temperature Sensor Count | 0x36 | 2 | bit 54 | 温感数不匹配 | Mismatched Temperature Sensor Count | 0x36 | 3
| bit 55 | 供电电压异常 | Supply Voltage Anomaly | 0x37 | 1 | bit 55 | 供电电压异常 | Supply Voltage Anomaly | 0x37 | 2 | bit 55 | 供电电压异常 | Supply Voltage Anomaly | 0x37 | 3
| bit 56 | 碰撞故障 | Collision Fault | 0x38 | 1 | bit 56 | 碰撞故障 | Collision Fault | 0x38 | 2 | bit 56 | 碰撞故障 | Collision Fault | 0x38 | 3
| bit 57 | 未并簇（总正总负继电器未闭合） | Cluster Not Paralleled (Main Positive/Negative Contactor Not Closed) | 0x39 | 1 | bit 57 | 未并簇（总正总负继电器未闭合） | Cluster Not Paralleled (Main Positive/Negative Contactor Not Closed) | 0x39 | 2 | bit 57 | 未并簇（总正总负继电器未闭合） | Cluster Not Paralleled (Main Positive/Negative Contactor Not Closed) | 0x39 | 3
| bit 58 | 预留 | Reserved | 0x3A | 1 | bit 58 | 预留 | Reserved | 0x3A | 2 | bit 58 | 预留 | Reserved | 0x3A | 3
| bit 59 | 预留 | Reserved | 0x3B | 1 | bit 59 | 预留 | Reserved | 0x3B | 2 | bit 59 | 预留 | Reserved | 0x3B | 3
| bit 60 | 预留 | Reserved | 0x3C | 1 | bit 60 | 预留 | Reserved | 0x3C | 2 | bit 60 | 预留 | Reserved | 0x3C | 3
| bit 61 | 预留 | Reserved | 0x3D | 1 | bit 61 | 预留 | Reserved | 0x3D | 2 | bit 61 | 预留 | Reserved | 0x3D | 3
| bit 62 | 预留 | Reserved | 0x3E | 1 | bit 62 | 预留 | Reserved | 0x3E | 2 | bit 62 | 预留 | Reserved | 0x3E | 3
| bit 63 | 预留 | Reserved | 0x3F | 1 | bit 63 | 预留 | Reserved | 0x3F | 2 | bit 63 | 预留 | Reserved | 0x3F | 3
|  | 预留 | Reserved | 0x40~0xFF | 1 |  | 预留 | Reserved | 0x40~0xFF | 2 |  | 预留 | Reserved | 0x40~0xFF | 3
Stack fault code | Level 1 Fault（ 0x1300~0x13FF） |  |  |  |  | Level 2 Fault（0x1400~0x14FF） |  |  |  |  | Level 3 Fault（0x1500~0x15FF）
| Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level | Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level | Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level
| bit 0 | 簇间环流故障 | Inter-Cluster Circulating Current Fault | 0x00 | 1 | bit 0 | 簇间环流故障 | Inter-Cluster Circulating Current Fault | 0x00 | 2 | bit 0 | 簇间环流故障 | Inter-Cluster Circulating Current Fault | 0x00 | 3
| bit 1 | 簇间压差过大 | Excessive Inter-Cluster Voltage Difference | 0x01 | 1 | bit 1 | 簇间压差过大 | Excessive Inter-Cluster Voltage Difference | 0x01 | 2 | bit 1 | 簇间压差过大 | Excessive Inter-Cluster Voltage Difference | 0x01 | 3
| bit 2 | 并网失败故障 | Grid Connection Failure Fault | 0x02 | 1 | bit 2 | 并网失败故障 | Grid Connection Failure Fault | 0x02 | 2 | bit 2 | 并网失败故障 | Grid Connection Failure Fault | 0x02 | 3
| bit 3 | 簇通信丢失 | Cluster Communication Lost | 0x03 | 1 | bit 3 | 簇通信丢失 | Cluster Communication Lost | 0x03 | 2 | bit 3 | 簇通信丢失 | Cluster Communication Lost | 0x03 | 3
| bit 4 | 缺簇运行（最小并簇数＜实际并簇数＜满簇数量） | Cluster Under-Run (Min Parallel Cluster Count < Actual Parallel Cluster Count < Full Cluster Count) | 0x04 | 1 | bit 4 | 缺簇运行（0＜实际并簇数＜最小并簇数） | Cluster Under-Run (0<Actual Parallel Cluster Count<Minimum Parallel Cluster Count) | 0x04 | 2 | bit 4 | 缺簇运行（实际并簇数=0） | Cluster Under-Run (Actual Parallel Cluster Count = 0) | 0x04 | 3
| bit 5 | 预留 | Reserved | 0x05 | 1 | bit 5 | 预留 | Reserved | 0x05 | 2 | bit 5 | 预留 | Reserved | 0x05 | 3
| bit 6 | 预留 | Reserved | 0x06 | 1 | bit 6 | 预留 | Reserved | 0x06 | 2 | bit 6 | 预留 | Reserved | 0x06 | 3
| bit 7 | 预留 | Reserved | 0x07 | 1 | bit 7 | 预留 | Reserved | 0x07 | 2 | bit 7 | 预留 | Reserved | 0x07 | 3
|  | 预留 | Reserved | ~0xFF |  |  | 预留 | Reserved | ~0xFF |  |  | 预留 | Reserved | ~0xFF
EMS fault code | Level 1 Fault（ 0x1600~0x16FF） |  |  |  |  | Level 2 Fault（ 0x1700~0x17FF） |  |  |  |  | Level 3 Fault（ 0x1800~0x18FF）
| Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level | Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level | Bit Index | 故障名称 | Fault Description | Fault Sub-code | Fault Level
| bit 0 | 簇故障 | Cluster Fault | 0x00 | 1 | bit 0 | 簇故障 | Cluster Fault | 0x00 | 2 | bit 0 | 簇故障 | Cluster Fault | 0x00 | 3
| bit 1 | 堆故障 | Stack Fault | 0x01 | 1 | bit 1 | 堆故障 | Stack Fault | 0x01 | 2 | bit 1 | 堆故障 | Stack Fault | 0x01 | 3
| bit 2 | 逆变器故障 | Inverter Fault | 0x02 | 1 | bit 2 | 逆变器故障 | Inverter Fault | 0x02 | 2 | bit 2 | 逆变器故障 | Inverter Fault | 0x02 | 3
| bit 3 | 电表故障 | Meter Fault | 0x03 | 1 | bit 3 | 电表故障 | Meter Fault | 0x03 | 2 | bit 3 | 电表故障 | Meter Fault | 0x03 | 3
| bit 4 | 门禁故障 | Access Control Fault | 0x04 | 1 | bit 4 | 门禁故障 | Access Control Fault | 0x04 | 2 | bit 4 | 门禁故障 | Access Control Fault | 0x04 | 3
| bit 5 | 消防故障 | Firefighting Fault | 0x05 | 1 | bit 5 | 消防故障 | Firefighting Fault | 0x05 | 2 | bit 5 | 消防故障 | Firefighting Fault | 0x05 | 3
| bit 6 | 空调故障 | AC Unit Fault | 0x06 | 1 | bit 6 | 空调故障 | AC Unit Fault | 0x06 | 2 | bit 6 | 空调故障 | AC Unit Fault | 0x06 | 3
| bit 7 | 急停故障 | Emergency Stop Fault | 0x07 | 1 | bit 7 | 急停故障 | Emergency Stop Fault | 0x07 | 2 | bit 7 | 急停故障 | Emergency Stop Fault | 0x07 | 3
|  | 预留 | Reserved | ~0xFF |  |  | 预留 | Reserved | ~0xFF |  |  | 预留 | Reserved | ~0xFF
DI equipment | DI Analysis（ 0x4200~0x4225）
| Bit Index | 名称 | Description | Sub-code
| bit 0 | 无 | None | 0x00
| bit 1 | 急停触发 | Emergency Stop Triggered | 0x01
| bit 2 | 消防触发 | Firefighting Triggered | 0x02
| bit 3 | 温感触发 | Temperature Sensor Triggered | 0x03
| bit 4 | 门禁触发 | Access Control Triggered | 0x04
| bit 5 | 水浸触发 | Water Immersion Triggered | 0x05
| bit 6 | 烟感触发 | Smoke Sensor Triggered | 0x06
| bit 7 | DC防雷 | DC Lightning Protection | 0x07
| bit 8 | AC防雷 | AC Lightning Protection | 0x08
| bit 9 | 隔离开关断开 | Isolating Switch Disconnected | 0x09
| bit 10 | 消防火警 | Fire Alarm | 0x0A
| bit 11 | 消防启动 | Firefighting Start | 0x0B
| bit 12 | 消防故障 | Firefighting Fault | 0x0C
bit 13
bit 14
bit 15
bit 16
bit 17
bit 18
bit 19
bit 20
bit 21
bit 22
bit 23
bit 24
bit 25
bit 26
bit 27
bit 28
bit 29
bit 30
bit 31